## PHS
Pumped Hydro Storage
| 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2030) |  | Note | Ref
Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
Form of energy stored | Mechanical / hydraulic
Application | Energy Shifting/ 8h
Energy storage capacity for one unit (MWh) | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 |  | [1]
Output capacity for one unit (MW) | 1060 | 1060 | 1060 | 1060 | 1060 | 1060 | 1060 |  | [1]
Input capacity for one unit (MW) | 1060 | 1060 | 1060 | 1060 | 1060 | 1060 | 1060 |  | [1]
Round trip efficiency AC-AC (%) | 78 | 80 | 80 | 68.25 | 81.9 | 68.25 | 81.9 | A | [2], [3], [4], [5], [6], [7]
- Charge efficiency (%) | 88.3176 | 89.4427 | 89.4427 | 82.6136 | 90.4986 | 82.6136 | 90.4986
- Discharge efficiency (%) | 88.3176 | 89.4427 | 89.4427 | 82.6136 | 90.4986 | 82.6136 | 90.4986
Energy losses during storage (%/day) | 0.01 | 0.01 | 0.01 | 0.001 | 0.02 | 0.001 | 0.02 |  | [5]
Auxiliary electricity consumption (% of output) | < 0,01 | < 0,01 | < 0,01 | < 0,01 | < 0,01 | < 0,01 | < 0,01
Forced outage (%) | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | [3]
Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | [3]
Technical lifetime (years) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | A | [2], [4], [6]
Construction time (years) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | A | [3], [7]
Lifetime (total number of cycles) | 33250 | 33250 | 33250 | 26100 | 40300 | 26100 | 40300 |  | [7]
Regulation ability
Response time from idle to full-rated discharge (sec) | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | [8]
Response time from full-rated charge to full-rated discharge (sec) | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | [8]
Financial data
Specific investment (MUSD 2020 per MWh) | 0.12775 | 0.12775 | 0.12775 | 0.070471 | 0.34941 | 0.070471 | 0.34941 | B | [1]
-Energy component (MUSD/MWh) | 0.023 | 0.023 | 0.023 | 0.005 | 0.1 | 0.005 | 0.1 | C | [1]
-Capacity component (MUSD/MW) | 0.84 | 0.84 | 0.84 | 0.525 | 2 | 0.525 | 2 | D | [1]
Fixed O&M (kUSD2020/MW/year) | 5.106 | 5.106 | 5.106 | 2.22 | 10.212 | 2.22 | 10.212 |  | [9]
Variable O&M (USD2020/MWh/year) | 0.242 | 0.242 | 0.242 | 0.209 | 0.924 | 0.209 | 0.924 |  | [9]
Technology specific data
Specific investment (USD2020/MW) | 1.0244 | 1.0244 | 1.0244 | 0.56509 | 2.8019 | 0.56509 | 2.8019 |  | [1]
Notes
A | Data average with data of the references
B | This data is interpreted within the IRENA tool as: "Total Invest per usable kWh storage", and is verifiable as a result of : Energy Storage + Power Conversion/Usable Storage Capacity.
C | This data is interpreted within the IRENA tool as: "Energy Installation cost". But also estimated by: Total Storage Invest/Usable Storage Capacity
D | This data is interpreted within the IRENA tool as: "Power Installation cost". but also estimated by: Total conversion Invest/Installed Conversión Power
References
[1] | IRENA (2017). Electricity storage and renewables: Costs and markets to 2030. Cost of service tool. Available in: https://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[2] | Gür, T. M. (2018). Review of electrical energy storage technologies, materials and systems: Challenges and prospects for large-scale grid storage. Energy and Environmental Science, 11(10), 2696–2767. https://doi.org/10.1039/c8ee01419a
[3] | Lazard levelized cost of storage 2016
[4] | Barbour, E., Wilson, I. A. G., Radcliffe, J., Ding, Y., & Li, Y. (2016). A review of pumped hydro energy storage development in significant international electricity markets. Renewable and Sustainable Energy Reviews, 61, 421–432. https://doi.org/10.1016/j.rser.2016.04.019
[5] | IRENA. (2017). Electricity Storage and Renewables: Cost and Markets to 2030. Retrieved from https://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[6] | Luo, X., Wang, J., Dooner, M., & Clarke, J. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation. Applied Energy, 137, 511–536. https://doi.org/https://doi.org/10.1016/j.apenergy.2014.09.081
[7] | Schmidt, O., Melchior, S., Hawkes, A., & Staffell, I. (2019). Projecting the Future Levelized Cost of Electricity Storage Technologies. Joule, 3(1), 81–100. https://doi.org/10.1016/j.joule.2018.12.008
[8] | European Energy Research Alliance, Fact Sheet Pumped Hydro Energy Storage, Nov 2016. Retrieved from https://eera-es.eu/wp-content/uploads/2016/03/EERA_Factsheet_Pumped-Hydro-Energy-Storage.pdf
[9] | B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
[10] | Danish Energy Agency. (2019). Technogy Data for Energy Storage. Copenhagen, Denmark. Retrieved from https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_energy_storage.pdf

## Data
[5 empty] | Exchange ratio between the years 2030 and 2020 |  | Exchange ratio between the years 2050 and 2030
Technical Data | 2016 | 2020 | 2025 | 2030 | 30 - 20 | 2050 |  | Reference | Prodecure followed to determine the projection
Energy Storage Capacity for One Unit (MWh) | 8500 | 8500 | 8500 | 8500 |  | 8500 |  | [1] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [10] for PHS. 2. This data is interpreted within the IRENA tool as "Usable Storage Capacity" and "Installed Storage". 3. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Output Capacity for One Unit (MW) | 1060 | 1060 | 1060 | 1060 |  | 1060
Input Capacity for One Unit (MW) | 1060 | 1060 | 1060 | 1060 |  | 1060
Round Trip Efficiency (%) |  | 78 |  | 80 |  | 80 |  | [10] | 1. The trend of the data for this parameter (in this case constant) was identified in reference [10] for PHS. 2. The data of years 2020, 2030, and 2050 were obtained from [10].
Charge Efficiency (%) |  | 88.3176 |  | 89.4427 |  | 89.4427 |  |  | 1. This technical data was calculated with an equation for Round Trip Efficiency. 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Round Trip Efficiency.
Discharge Efficiency (%) |  | 88.3176 |  | 89.4427 |  | 89.4427
Energy Losses during Storage (%/day) | 0.01 | 0.01 |  | 0.01 |  | 0.01 |  | [1] | 1. The trend of the data for this parameter (in this case constant) was identified in reference [10] for PHS. 2. The data of years 2020 and 2030 was obtained from [1]. 3. It is considered these parameters will not have a variation in the period 2030-2050 due it technological maturity.
Forced Outage (%) |  | 2 | [5 empty] | [3] | 1. The data for 2020 is a point data types for this year from [3] 2. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Planned Outage (weeks per year) |  | 1
Technical Lifetime (years) |  | 60 |  | 60 |  | 60 |  | [2,4,6] | 1. The data for 2020 in the sheet called "PHS" is the average of several authors (as shown [2], [4], [6]). 2. The trend of the data for this parameter (in this case constant) was identified in reference [10] for PHS. 3. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Construction Time (years) |  | 5 | [5 empty] | [3], [7] | 1. The data for 2020 in the sheet called "PHS" is the average of several authors (as shown [3], [7]). 2. It is considered this parameter will not have a variation in the period 2020-2050 due it technological maturity.
Lifetime in Total Number of Cycle |  | 33250 | [5 empty] | [7] | 1. The data for the year 2020 was obtained from [7]. 2. It is considered this parameter will not have a variation in the period 2020-2050 due it technological maturity.
Response Time from Idle to Full-Rated Discharge (sec) |  | 120 | [5 empty] | [8] | 1. The data of year 2020 was obtained from [8]. 2. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Response Time from Full-Rated Charge to Full-Rated Discharge (sec) |  | 300
Specific Investment (MUSD2020 per MWh) |  | 0.12775 |  | 0.12775 |  | 0.12775 |  | [1] | 1. This parameter data was calculated with an equation for Specific Investment. 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Investment.
Energy Component (MUSD2015 per MWh) | 0.023 | 0.023 | 0.023 | 0.023 |  | 0.023 |  |  | 1. The trend of the data for these parameters (in this case constant) was identified in reference [10] for PHS. 2. The data of years 2016, 2020, 2025, and 2030 was obtained from [1].
Capacity Component (MUSD per MW) | 0.84 | 0.84 | 0.84 | 0.84 |  | 0.84
Fixed O&M (MUSD2020/MW/year) |  | 5.1 |  | 5.1 |  | 5.1 |  | [9] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [10] for PHS. 2. The data the year 2020 was obtained from [9]. 3. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Variable O&M (MUSD2020/MW/year) |  | 0.242 |  | 0.242 |  | 0.242
Specific Investment (MUSD2020 per MW) |  | 1.0244 |  | 1.0244 |  | 1.0244 |  |  | 1. This parameter data was calculated with an equation for Specific Investment. 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Investment.
[1] | IRENA (2017). Electricity storage and renewables: Costs and markets to 2030. Cost of service tool. Available in: https://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[2] | Gür, T. M. (2018). Review of electrical energy storage technologies, materials and systems: Challenges and prospects for large-scale grid storage. Energy and Environmental Science, 11(10), 2696–2767. https://doi.org/10.1039/c8ee01419a
[3] | Lazard levelized cost of storage 2016
[4] | Barbour, E., Wilson, I. A. G., Radcliffe, J., Ding, Y., & Li, Y. (2016). A review of pumped hydro energy storage development in significant international electricity markets. Renewable and Sustainable Energy Reviews, 61, 421–432. https://doi.org/10.1016/j.rser.2016.04.019
[5] | IRENA. (2017). Electricity Storage and Renewables: Cost and Markets to 2030. Retrieved from https://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[6] | Luo, X., Wang, J., Dooner, M., & Clarke, J. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation. Applied Energy, 137, 511–536. https://doi.org/https://doi.org/10.1016/j.apenergy.2014.09.081
[7] | Schmidt, O., Melchior, S., Hawkes, A., & Staffell, I. (2019). Projecting the Future Levelized Cost of Electricity Storage Technologies. Joule, 3(1), 81–100. https://doi.org/10.1016/j.joule.2018.12.008
[8] | European Energy Research Alliance, Fact Sheet Pumped Hydro Energy Storage, Nov 2016. Retrieved from https://eera-es.eu/wp-content/uploads/2016/03/EERA_Factsheet_Pumped-Hydro-Energy-Storage.pdf
[9] | B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
[10] | Danish Energy Agency. (2019). Technogy Data for Energy Storage. Copenhagen, Denmark. Retrieved from https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_energy_storage.pdf

## Uncertanties
[5 empty] | 2020 (Uncertainty) |  | 2050 (Uncertainty) |  |  | Exchange ratio 2020 |  | Exchange ratio 2030 |  | Exchange ratio 2050 |  |  |  |  | NOTE
Technical Data | ABB | 2020 | 2030 | 2050 | Lower | Upper | Lower | Upper | Reference | Lower | Upper | Lower | Upper | Lower | Upper |  |  |  | 1. The uncertainty is calculated with the similar numerical behaviour from [3]. 2. The exchange ratio for 2030 is estimated by linear regression between the exchange ratio 2020 and 2050.
Energy Storage Capacity for One Unit (MWh) | ESC | 1600 | 1600 | 1600 | 400 | 8000 | 400 | 8000 | [10] | -0.75 | 4 | -0.75 | 4 | -0.75 | 4
Output Capacity for One Unit (MW) | OCO | 200 | 200 | 200 | 50 | 1000 | 50 | 1000 |  | -0.75 | 4 | -0.75 | 4 | -0.75 | 4
Input Capacity for One Unit (MW) | ECO | 200 | 200 | 200 | 50 | 500 | 50 | 500 |  | -0.75 | 1.5 | -0.75 | 1.5 | -0.75 | 1.5
Round Trip Efficiency (%) | RTE | 80 | 80 | 80 | 70 | 84 | 70 | 84 |  | -0.125 | 0.05 | -0.125 | 0.05 | -0.125 | 0.05 | Year | Lower (%) | Upper (%)
Energy Losses during Storage (%/day) | ELS | 1 | 1 | 1 | 0.1 | 2 | 0.1 | 2 |  | -0.9 | 1 | -0.9 | 1 | -0.9 | 1 | 2020 | -0.75 | 0
Idle to Full Discharge (sec) | IFD | 240 | 60 | 60 | 60 | 240 | 60 | 240 |  | -0.75 | 0 | -0.5 | 1 | 0 | 3 | 2050 | 0 | 3
NOTE
- Charge efficiency (%) | 1. The uncertainty was calculated with an equation for Round Trip Efficiency. 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Round Trip Efficiency.
- Discharge efficiency (%)
Forced outage (%) | 1. The uncertainty for these parameters has the same behaviour to [3] to keep the consistency between data.
Planned outage (weeks per year)
Construction time (years) | 1. The uncertainty for these parameters has the same behaviour to [3, 7] to keep the consistency between data.
Technical Lifetime (years) | 1. The uncertainty for these parameters has the same behaviour to [2, 4, 6] to keep the consistency between data.
Specific investment (MUSD2020 per MWh) | 1. This parameter data was calculated with an equation for Specific Investment. 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Investment.
-Energy component (MUSD2020/MWh) | 1. The uncertainty for these parameters has the same behaviour to [1] to keep the consistency between data.
-Capacity component (MUSD2020/MW)
Fixed O&M (MUSD2020/MW/year) | 1. The uncertainty for these parameters has the same behaviour to [9] to keep the consistency between data.
Variable O&M (USD2020/MWh/year)
Specific investment (MUSD2020 per MW) | 1. This parameter data was calculated with an equation for Specific Investment. 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Investment.
Lifetime in total number of cycles | 1. The uncertainty for these parameters has the same behaviour to [7] to keep the consistency between data.