## Lithium Ion
| Technology |  | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135)
|  | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2030) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Form of energy stored | Electrochemical
| Application | System, energy-intensive (2 h)
| Energy storage capacity for one unit (MWh) | 6 | 7 | 8 | 5 | 9 | 5.9321 | 10.5 | A | [1, 6]
| Output capacity for one unit (MW) | 3 | 3.5 | 4 | 2.6667 | 3.5 | 3.144 | 4.0833 | A | [1, 6]
| Input capacity for one unit (MW) | 3 | 3.5 | 4 | 2.6667 | 3.5 | 3.144 | 4.0833 | A | [1, 6]
| Round trip efficiency (%) AC | 92 | 93.011 | 93.011 | 90.989 | 93.011 | 91.9889 | 94.3027 | B | [2, 8, 9, 17]
| Round trip efficiency (%) DC | 96.04 | 97.0276 | 97.0276 | 96.04 | 97.0225 | 96.7751 | 98.0151 | B | [2, 8, 9, 17]
| - Charge efficiency (%) | 98 | 98.5 | 98.5 | 98 | 98.5 | 98.3743 | 99.0026 | C | [1]
| - Discharge efficiency (%) | 98 | 98.5052 | 98.5052 | 98 | 98.5 | 98.3743 | 99.0026 | C | [1]
| Energy losses during storage (%/day) | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.18327 | D | [7, 16, 18]
| Forced outage (%) | 0.38 | 0.35 | 0.32237 | 0.2 | 0.5 | 0.16914 | 0.44677 | E
| Planned outage (weeks per year) | 0.2 | 0.1 | 0.05 | 0.1 | 0.25 | 0.05 | 0.15 | E
| Technical lifetime (years) | 20 | 25 | 31.25 | 15 | 25 | 18.0443 | 33.3164 | F | [2, 4, 5, 6]
| Construction time (years) | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.16653 | 0.25 |  | [11]
| Lifetime in total number of cycles | 14000 | 30000 | 50000 | 10000 | 16000 | 18200 | 36800 | P | [2-4, 6]
Regulation ability
| Response time from idle to full-rated discharge (sec) | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | G | [19]
| Response time from full-rated charge to full-rated discharge (sec) | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | <0.08 | G | [19]
Financial data
| Specific investment (MUSD2020 per MWh) | 0.40737 | 0.26421 | 0.17488 | 0.31968 | 0.55204 | 0.19725 | 0.50705 | H | [14, 15]
| - energy component (MUSD/MWh) | 0.14652 | 0.085501 | 0.049894 | 0.0777 | 0.20979 | 0.051375 | 0.17534 |  | [14]
| - capacity component (MUSD/MW) PCS | 0.2997 | 0.17982 | 0.10789 | 0.2664 | 0.5661 | 0.14667 | 0.47622 |  | [23]
| - other project costs (MUSD/MWh) | 0.111 | 0.0888 | 0.07104 | 0.0999 | 0.1221 | 0.06814 | 0.14652 | J | [9, 12, 20]
| Fixed O&M (kUSD2020/MW/year) | 0.54 | 0.54 | 0.54 | 0.45 | 0.54 | 0.43379 | 0.54 | K | [23]
| Variable O&M (USD2020/MWh) | 2.22 | 1.998 | 1.7982 | 0.444 | 6.216 | 0.38992 | 4.7702 | L | [21]
Technology specific data
| Energy storage expansion cost (M$2020/MWh) | 0.25752 | 0.1743 | 0.12093 | 0.1776 | 0.33189 | 0.11952 | 0.32186 | M | [14, 15]
| Output capacity expansion cost (M$2020/MW) | 0.2997 | 0.17982 | 0.10789 | 0.2664 | 0.5661 | 0.14667 | 0.47622 | N | [20-22]
| Alternative Investment cost (M$2020/MW) | 0.3663 | 0.222 | 0.13455 | 0.3108 | 0.6438 | 0.17205 | 0.54696 | O | [13, 14, 15, 20-22]
| Specific power (W/kg) | 57.6923 | 67.3077 | 76.9231 | 56.8498 | 59.8291 | 61.0387 | 71.5344 | Q | [1, 10]
| Power density (kW/m3) | 68.9013 | 80.3849 | 91.8684 | 68.4067 | 82.446 | 71.7983 | 96.187 | Q | [1, 10]
| Specific energy (Wh/kg) | 115.3846 | 134.6154 | 153.8462 | 106.5934 | 153.8462 | 115.1668 | 183.9456 | Q | [1, 10]
| Energy density (kWh/m3) | 137.8027 | 160.7698 | 183.7369 | 128.2625 | 212.0041 | 135.4678 | 247.3381 | Q | [1, 10]
| Exchange Rate (USD/EUR) | 1.11
Notes
A. One unit defined as a 40 feet container including LIB system and excluding power conversion system. Values for 2015-2030 are taken from Samsung SDI brochures for grid-connected LIBs from 2016 and 2018 [1,6]. This unit of 6MWh/3MW (0.5C) is a typical size grid scale battery for energy shift and peak shaving. The Specific investment cost under financial data is provided for a 1MWh : 0.5MW (0.5C) battery. Cost examples of a 2MWh/8MW and a 16MWh/4MW battery are given in the section below.
B. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90% [8,9].
C. The C-rate is 0.5 during charge and can be up to 6 during discharge for the Samsung SDI batteries [1,6]. The presented conversion efficiencies assume average charge and discharge C-rates in 2015-2020 around 0.5. Higher C-rates during discharge will slightly decrease the efficiency.
D. Lithium-ion battery daily discharge loss. The central estimates for self-discharge of Li-ion batteries range between 0.05% and 0.20% a day in 2016 and are expected to stay flat to 2030.
E. It is expected not to have any outage during lifetime of the grid-connected LIB. Only a few days during the e.g. 15 years life time is needed for service and exchanging fans and blowers for thermal management system and power conversion system. Forced outage is expected to drop with increasing robustness following the learning rate and cumulated production. Planned outage is expected to decrease due to increased automation.
F. Current state-of-the-art NMC LIB has 20 years lifetime. The NMC lifetime is expected to have LTO lifetime by 2020 and 30 years lifetime for grid-connected LIBs in 2040 and 2050 as photovoltaic power systems have today [2,4,5,6].
G. The response time is obtained from simulated response time experiments with hardware in the loop [19].
H. The system specific forecasts includes rack, TMS, BMS, EMS and PCS. The forecast is calculated as the sum of the PCS, the battery cell, and other costs. The system specific forecast is exclusive power cables to the site and entrepreneur work for installation of the containers [14,15]. The specific investment cost is the total cost of a 1MWh : 0.5MW (0.5C) battery.
I. Power conversion cost is strongly dependent on scalability and application. The PCS cost is based on references [20-22] and reflects the necessity for high power performance and compliance to grid codes to provide ancillary services, bidirectional electricity flow and two-stage conversion, as well as the early stage of development and the fact that few manufacturers can guarantee turnkey systems. Inverter replacement is expected every 10 years. The bidirectional inverter given here has more or less the same charge and discharge capacity (MW).
J. Other costs include construction costs and entrepreneur work. These costs heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards. Estimates are aggregated from the literature [9,12,20].
K. Fixed O&M is assumed to be constant, although the O&M may depend on the application [9].
L. Variable O&M is assumed to be 2.3 USD/MWh in 2015 with a range of 0.4 – 5.6 [21].
M. Since multi-MWh LIB systems are scalar, the energy storage expansion cost is here estimated to be equal to the energy component plus the “other costs” [14,15].
N. Since multi-MW LIB systems are scalar, the capacity expansion cost equals the capacity component cost [20-22].
O. The alternative investment cost in MUSD2015/MW is specified for a 4C, 0.25 h system as for the Laurel Mountain, West Virginia, USA grid-scale LIB storage system [13]. I.e. the alternative investment cost is 25% of the energy storage expansion cost plus the PCS cost [13,14,15,20-22].
P. Cycle life specified as the number of cycles at 1C/1C to 80% state-of-health. Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C/2 to 3C [6]. Steady improvement in battery lifetime due to better materials and battery management is expected. Kokam ESS solutions are also rated at more than 8000-20000 cycles (80-90% DOD) based on chemistry [2]. Thus for daily full charge-discharge cycles, the batteries are designed to last for 15-50 years if supporting units are well functioning. Lifetimes are given for both graphite and LTO anode based commercial batteries from Kokam. Cycle lives are steadily increasing over last few years as reflected in 2020/2030 numbers [3,4,6].
Q. Specific power, power density, Specific energy and energy density is provided for 0.5C reflecting the energy and power capacity in the datasheet. The expected development depends on the successive R&D progress[1,10].
References
1 | Samsung. ESS Batteries by Samsung SDI Top Safety & Reliability Solutions, (2018). http://www.samsungsdi.com/upload/ess_brochure/201809_SamsungSDI ESS_EN.pdf
2 | L. Kokam Co. Total Energy Storage Solution Provider, (2018). http://kokam.com/data/2018_Kokam_ESS_Brochure_ver_5.0.pdf
3 | L. Kokam Co. Kokam Li-ion / Polymer Cell, (2017). http://kokam.com/data/Kokam_Cell_Brochure_V.4.pdf
4 | StoraXe. StoraXe Industrial & Infrastructure Scalable battery storage system, (2018). https://www.ads-tec.de/fileadmin/download/doc/brochure/Datasheet_Energy_Industrial_EN.pdf
5 | Altairnano. 24 V 60 Ah Battery Module, (2016). https://altairnano.com/products/battery-module/
6 | Samsung, Smart Battery Systems for Energy Storage, (2016). http://www.samsungsdi.com/upload/ess_brochure/Samsung SDI brochure_EN.pdf
7 | Electropaedia. Battery Performance Characteristics - How to specify and test a battery, (2018). https://www.mpoweruk.com/performance.htm
8 | A.H. Fathima, K. Palanisamy. Renewable systems and energy storages for hybrid systems, Ed(s): A. Hina Fathima, et al., in Hybrid-renewable energy systems in microgrids. Woodhead Publishing (2018), pp. 162. https://doi.org/10.1016/B978-0-08-102493-5.00008-X
9 | Lazard. Levelized Cost of Storage (2017)., https://www.lazard.com/perspective/levelized-cost-of-storage-2017/
10 | LG Chem. Change your energy. Change your life., (2018). http://www.lgchem.com/upload/file/product/LGChem_Catalog_Global_2018.pdf
11 | Tesla. Addressing Peak Energy Demand with the Tesla Powerpack, (2016). https://www.tesla.com/da_DK/blog/addressing-peak-energy-demand-tesla-powerpack?redirect=no
12 | Tesla. Tesla Powerpack to Enable Large Scale Sustainable Energy to South Australia, (2017). https://www.tesla.com/da_DK/blog/Tesla-powerpack-enable-large-scale-sustainable-energy-south-australia?redirect=no Page
13 | Energy Storage Association. Frequency Regulation Services and a Firm Wind Product: AES Energy Storage Laurel Mountain Battery Energy Storage, (2018). http://energystorage.org/energy-storage/case-studies/frequency-regulation-services-and-firm-wind-product-aes-energy-storage
14 | Bloomberg New Energy Finance. New Energy Outlook 2018, (2018). https://bnef.turtl.co/story/neo2018.pdf?autoprint=true&teaser=true
15 | International Renewable Energy Agency. IRENA Battery Storage Report, (2015). http://www.irena.org/-/media/Files/IRENA/Agency/Publication/2015/IRENA_Battery_Storage_report_2015.pdf
16 | International Renewable Energy Agency. Electricity Storage and Renewables : Costs and Markets To 2030, (2017). http://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
17 | Danish Technological Institute. BESS project Smart grid ready Battery Energy Storage System for future grid, (2017). https://www.energiforskning.dk/sites/energiteknologi.dk/files/slutrapporter/bess_final_report_forskel_10731.pdf
18 | H. Chen, T.N. Cong, W. Yang, C. Tan, Y. Li, Y. Ding, Progress in electrical energy storage system: A critical review, Prog. Nat. Sci. 19 (2009) 291–312. doi:10.1016/j.pnsc.2008.07.014
19 | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127. doi:10.1016/j.apenergy.2017.06.046
20 | R. Benato, G. Bruno, F. Palone, R.M. Polito, M. Rebolini, Large-scale electrochemical energy storage in high voltage grids: Overview of the Italian experience, Energies. 10 (2017) 1-17. doi:10.3390/en10010108
21 | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596. doi:10.1016/j.rser.2014.10.011
22 | G. Huff, A.B. Currier, B.C. Kaun, D.M. Rastler, S.B. Chen, D.T. Bradshaw, W.D. Gauntlett, DOE/EPRI electricity storage handbook in collaboration with NRECA, (2015). https://www.sandia.gov/ess-ssl/publications/SAND2015-1002.pdf
23 | Danish Energy Agency. (2019). Technogy Data for Energy Storage. Copenhagen, Denmark. Retrieved from https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_energy_storage.pdf

## Data
|  |  |  | Exchange ratio between the years 2030 and 2020 |  | Exchange ratio between the years 2050 and 2030 |  | Prodecure followed to determine the projection | Projection in according with the exchange ratio (2030-2020 and 2050-2030)
Technical Data | 2015 | 2020 | 2030 | 20-30 (%) | 2050 | 30-50 (%) | Reference |  | 2020 | 2030 | 2050 | C-rate
Energy Storage Capacity for One Unit (MWh) | 3.2 | 6 | 7 | 0.16667 | 8 | 0.14286 | [23] | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [1, 6]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [1, 6] | 6 | 7 | 8
Output Capacity for One Unit (MW) | 9.6 | 18 | 21 | 0.16667 | 24 | 0.14286 |  |  | 3 | 3.5 | 4 | 3
Input Capacity for One Unit (MW) | 1.6 | 3 | 3.5 | 0.16667 | 4 | 0.14286 |  |  | 3 | 3.5 | 4 | 0.5
Round Trip Efficiency (%) AC | 91 | 91 | 92 | 0.010989 | 92 | 0 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [2, 8, 9, 17]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [2, 8, 9, 17]. | 92 | 93.011 | 93.011
Round Trip Efficiency (%) DC | 95 | 95 | 96 | 0.010526 | 96 | 0 |  |  | 96.04 | 97.0509 | 97.0509
Charge Efficiency (%) | 98 | 98 | 98.5 | 0.005102 | 98.5 | 0 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [1]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [1]. | 98 | 98.5 | 98.5
Discharge Efficiency (%) | 97 | 97 | 97.5 | 0.0051546 | 97.5 | 0 |  |  | 98 | 98.5052 | 98.5052
Energy Losses during Storage (%/day) | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [7, 16, 18]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [7, 16, 18]. | 0.1 | 0.1 | 0.1
Forced Outage (%) | 0.4 | 0.38 | 0.35 | -0.078947 | 0.25 | -0.28571 | [23] | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The exchange ratio is contant to 2030 and 2050, because it will not have a variation due its technological maturity. | 0.38 | 0.35 | 0.32237
Planned Outage (weeks per year) | 0.2 | 0.2 | 0.1 | -0.5 | 0.1 | 0 |  |  | 0.2 | 0.1 | 0.05
Technical Lifetime (years) | 15 | 20 | 25 | 0.25 | 30 | 0.2 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [2, 4, 5, 6]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [2, 4, 5, 6]. | 20 | 25 | 31.25
Construction Time (years) | 0.25 | 0.2 | 0.2 | 0 | 0.2 | 0 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [11]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [11]. | 0.2 | 0.2 | 0.2
Response Time from Idle to Full-Rated Discharge (sec) |  | <0,08 | <0,08 |  | <0,08 |  | [19] | 1. The data of tha year 2020 is repeatead for 2030 and 2050 because it will not have a variation due to its technological maturity.
Response Time from Full-Rated Charge to Full-Rated Discharge (sec) |  | <0,08 | <0,08 |  | <0,08
Specific Investment (MUSD2015 per MWh) | [6 empty] | [24] | 1. This parameter data was calculated with an equation for Specific Investment (see Lithium Ion sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Investment.
Energy Component (MUSD2015 per MWh) | 1.365 | 0.79 | 0.461 | -0.41646 | 0.316 | -0.31453 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [24]. 2. The selected data for 2020 is a point data types from [14]. 3. The projections have similar numerical behavior to [24] with the estimated exchange ratio applied to estimated the projection of the value from [14]. | 0.14652 | 0.085501 | 0.049894
Capacity Component (MUSD per MW) | 0.32 | 0.3 | 0.18 | -0.4 | 0.07 | -0.61111 | [23] | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The exchange ratio is constant to 2030 and 2050, because it will not have a variation due its technological maturity. | 0.2997 | 0.17982 | 0.10789
Other Project Costs (ME/MWh) | 0.11 | 0.1 | 0.08 | -0.2 | 0.04 | -0.5 | [23] | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [9, 12, 20]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [9, 12, 20]. | 0.111 | 0.0888 | 0.07104
Fixed O&M (MUSD2020/MW/year) | 0.54 | 0.54 | 0.54 | 0 | 0.54 | 0 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The exchange ratio is constant to 2030 and 2050, because it will not have a variation due its technological maturity. 2. The projection is an exchange ratio because there is no historical data. | 0.54 | 0.54 | 0.54
Variable O&M (MUSD2020/MW/year) | 2.1 | 2 | 1.8 | -0.1 | 1.6 | -0.11111 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [21]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [21]. | 2.22 | 1.998 | 1.7982
Energy storage expansion cost (M$2015/MWh) | 0.418 | 0.232 | 0.142 | -0.38793 | 0.075 | -0.47183 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [14, 15]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [14, 15]. | 0.25752 | 0.15762 | 0.096474
Output capacity expansion cost (M$2015/MW) | 0.29 | 0.27 | 0.16 | -0.40741 | 0.06 | -0.625 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [20, 22]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [20, 22]. | 0.2997 | 0.1776 | 0.10524
Alternative Investment cost (M$2015/MW) | 0.39 | 0.33 | 0.2 | -0.39394 | 0.08 | -0.6 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [13, 14, 15, 20-22]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [13, 14, 15, 20-22]. | 0.3663 | 0.222 | 0.13455
Lifetime in total number of cycles | 6000 | 14000 | 30000 | 1.1429 | 50000 | 0.66667 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [2-4, 6]. 3. The projections have similar numerical behavior to [23] with the estimated exchange ratio applied to estimated the projection of the value from [2-4, 6]. | 14000 | 30000 | 50000
Specific power (W/kg) | 285 | 315 | 417 | 0.32381 | 627 | 0.5036 |  | 1. This technical data was calculated with a Specific Power equation (see Lithium Ion sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Power. | 57.6923 | 76.3736 | 101.1041
Power density (kW/m3) | 354 | 390 | 519 | 0.33077 | 780 | 0.50289 |  | 1. This technical data was calculated with a Power Density equation (see Lithium Ion sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Power Density. | 68.9013 | 91.6918 | 122.0206
Specific energy (Wh/kg) | 95 | 105 | 139 | 0.32381 | 209 | 0.5036 |  | 1. The data of years 2015, 2020, 2030, and 2050 showed in this sheets from [23]. 2. The selected data for 2020 is a point data types from [1, 10]. 4. The projections have a similar numerical behaviour to [23] with the value from [1,10] | 115.3846 | 152.7473 | 202.2083
Energy density (kWh/m3) | 118 | 130 | 173 | 0.33077 | 260 | 0.50289 |  |  | 137.8027 | 183.3835 | 244.0412
Cálculo de peso, volumen y energía para Specific Energy and Energy Density
|  | Weight: | Volume: |  |  |  | Energy:
|  | 1170 | 0.415 | m [W] | 0.97966 | m³ | 135 | kWh
|  |  | 1.067 | m [D]
|  |  | 2.2124 | m [H]
From [1]:
1 | Samsung. ESS Batteries by Samsung SDI Top Safety & Reliability Solutions, (2018). http://www.samsungsdi.com/upload/ess_brochure/201809_SamsungSDI ESS_EN.pdf
2 | L. Kokam Co. Total Energy Storage Solution Provider, (2018). http://kokam.com/data/2018_Kokam_ESS_Brochure_ver_5.0.pdf
3 | L. Kokam Co. Kokam Li-ion / Polymer Cell, (2017). http://kokam.com/data/Kokam_Cell_Brochure_V.4.pdf
4 | StoraXe. StoraXe Industrial & Infrastructure Scalable battery storage system, (2018). https://www.ads-tec.de/fileadmin/download/doc/brochure/Datasheet_Energy_Industrial_EN.pdf
5 | Altairnano. 24 V 60 Ah Battery Module, (2016). https://altairnano.com/products/battery-module/
6 | Samsung, Smart Battery Systems for Energy Storage, (2016). http://www.samsungsdi.com/upload/ess_brochure/Samsung SDI brochure_EN.pdf
7 | Electropaedia. Battery Performance Characteristics - How to specify and test a battery, (2018). https://www.mpoweruk.com/performance.htm
8 | A.H. Fathima, K. Palanisamy. Renewable systems and energy storages for hybrid systems, Ed(s): A. Hina Fathima, et al., in Hybrid-renewable energy systems in microgrids. Woodhead Publishing (2018), pp. 162. https://doi.org/10.1016/B978-0-08-102493-5.00008-X
9 | Lazard. Levelized Cost of Storage (2017)., https://www.lazard.com/perspective/levelized-cost-of-storage-2017/
10 | LG Chem. Change your energy. Change your life., (2018). http://www.lgchem.com/upload/file/product/LGChem_Catalog_Global_2018.pdf
11 | Tesla. Addressing Peak Energy Demand with the Tesla Powerpack, (2016). https://www.tesla.com/da_DK/blog/addressing-peak-energy-demand-tesla-powerpack?redirect=no
12 | Tesla. Tesla Powerpack to Enable Large Scale Sustainable Energy to South Australia, (2017). https://www.tesla.com/da_DK/blog/Tesla-powerpack-enable-large-scale-sustainable-energy-south-australia?redirect=no Page
13 | Energy Storage Association. Frequency Regulation Services and a Firm Wind Product: AES Energy Storage Laurel Mountain Battery Energy Storage, (2018). http://energystorage.org/energy-storage/case-studies/frequency-regulation-services-and-firm-wind-product-aes-energy-storage
14 | Bloomberg New Energy Finance. New Energy Outlook 2018, (2018). https://bnef.turtl.co/story/neo2018.pdf?autoprint=true&teaser=true
15 | International Renewable Energy Agency. IRENA Battery Storage Report, (2015). http://www.irena.org/-/media/Files/IRENA/Agency/Publication/2015/IRENA_Battery_Storage_report_2015.pdf
16 | International Renewable Energy Agency. Electricity Storage and Renewables : Costs and Markets To 2030, (2017). http://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
17 | Danish Technological Institute. BESS project Smart grid ready Battery Energy Storage System for future grid, (2017). https://www.energiforskning.dk/sites/energiteknologi.dk/files/slutrapporter/bess_final_report_forskel_10731.pdf
18 | H. Chen, T.N. Cong, W. Yang, C. Tan, Y. Li, Y. Ding, Progress in electrical energy storage system: A critical review, Prog. Nat. Sci. 19 (2009) 291–312. doi:10.1016/j.pnsc.2008.07.014
19 | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127. doi:10.1016/j.apenergy.2017.06.046
20 | R. Benato, G. Bruno, F. Palone, R.M. Polito, M. Rebolini, Large-scale electrochemical energy storage in high voltage grids: Overview of the Italian experience, Energies. 10 (2017) 1-17. doi:10.3390/en10010108
21 | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596. doi:10.1016/j.rser.2014.10.011
22 | G. Huff, A.B. Currier, B.C. Kaun, D.M. Rastler, S.B. Chen, D.T. Bradshaw, W.D. Gauntlett, DOE/EPRI electricity storage handbook in collaboration with NRECA, (2015). https://www.sandia.gov/ess-ssl/publications/SAND2015-1002.pdf
23 | Danish Energy Agency. (2019). Technogy Data for Energy Storage. Copenhagen, Denmark. Retrieved from https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_energy_storage.pdf
24 | Schmidt, O., Melchior, S., Hawkes, A., & Staffell, I. (2019). Projecting the Future Levelized Cost of Electricity Storage Technologies. Joule, 3(1), 81–100. https://doi.org/10.1016/j.joule.2018.12.008

## Uncertanties
[5 empty] | 2020 (Uncertainty) |  | 2050 (Uncertainty) |  |  | Exchange ratio 2020 |  | Exchange ratio 2030 |  | Exchange ratio 2050 |  | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%) | NOTE
Technical Data | ABB | 2020 | 2030 | 2050 | Lower | Upper | Lower | Upper | Reference | Lower | Upper | Lower | Upper | Lower | Upper | 2020 | -0.16667 | 0.5 | 2020 | -0.11111 | 0.16667 | 2020 | -0.010989 | 0.010989 | 1. The uncertainty is calculated with the similar numerical behaviour from [1]. 2. The exchange ratio for 2030 is estimated by linear regression between the exchange ratio 2020 and 2050.
Energy Storage Capacity for One Unit (MWh) | ESC | 6 | 7 | 8 | 5 | 9 | 7 | 12 | [23] | -0.16667 | 0.5 | -0.15255 | 0.5 | -0.125 | 0.5 | 2050 | -0.125 | 0.5 | 2050 | -0.083333 | 0.16667 | 2050 | -0.01087 | 0.021739
Output Capacity for One Unit (MW) | OCO | 18 | 21 | 24 | 16 | 21 | 22 | 28 |  | -0.11111 | 0.16667 | -0.1017 | 0.16667 | -0.083333 | 0.16667 | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%)
Round Trip Efficiency (%) AC | RTE | 91 | 92 | 92 | 90 | 92 | 91 | 94 |  | -0.010989 | 0.010989 | -0.010989 | 0.013888 | -0.01087 | 0.021739 | 2020 | 0 | 0.005102 | 2020 | -0.5 | 1 | 2020 | -0.47368 | 0.31579
Charge Efficiency (%) | CE | 98 | 98.5 | 98.5 | 98 | 98.5 | 98 | 99 |  | 0 | 0.005102 | -0.001276 | 0.005102 | -0.0050761 | 0.0050761 | 2050 | -0.0050761 | 0.0050761 | 2050 | -0.5 | 0.5 | 2050 | -0.6 | 0.2
Energy Losses during Storage (%/day) | ELS | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.15 |  | -0.5 | 1 | -0.5 | 0.83266 | -0.5 | 0.5 | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%)
Forced Outage (%) | FO | 0.38 | 0.35 | 0.25 | 0.2 | 0.5 | 0.1 | 0.3 |  | -0.47368 | 0.31579 | -0.51675 | 0.27648 | -0.6 | 0.2 | 2020 | -0.5 | 0.25 | 2020 | -0.25 | 0.25 | 2020 | 0 | 0.25
Planned Outage (weeks per year) | PO | 0.2 | 0.1 | 0.1 | 0.1 | 0.25 | 0.05 | 0.2 |  | -0.5 | 0.25 | -0.5 | 0.5 | -0.5 | 1 | 2050 | -0.5 | 1 | 2050 | -0.33333 | 0.5 | 2050 | -0.5 | 0.25
Technical Lifetime (years) | TL | 20 | 25 | 30 | 15 | 25 | 20 | 45 |  | -0.25 | 0.25 | -0.27823 | 0.33266 | -0.33333 | 0.5 | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%)
Construction Time (years) | CT | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.1 | 0.25 |  | 0 | 0.25 | -0.16734 | 0.25 | -0.5 | 0.25 | 2020 | -0.4697 | 0.43182 | 2020 | -0.11111 | 0.88889 | 2020 | -0.1 | 0.1
Energy Component (MUSD/MWh) | EC | 0.132 | 0.062 | 0.035 | 0.07 | 0.189 | 0.026 | 0.115 |  | -0.4697 | 0.43182 | -0.39912 | 1.0507 | -0.25714 | 2.2857 | 2050 | -0.25714 | 2.2857 | 2050 | -0.33333 | 3.1667 | 2050 | -0.5 | 1.75
Capacity Componenet (MUSD/MW) | CC | 0.27 | 0.16 | 0.06 | 0.24 | 0.51 | 0.04 | 0.25 |  | -0.11111 | 0.88889 | -0.18436 | 1.6483 | -0.33333 | 3.1667 | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%)
Other Project Cost (MUSD/MWh) | OPC | 0.1 | 0.08 | 0.04 | 0.09 | 0.11 | 0.02 | 0.11 |  | -0.1 | 0.1 | -0.23266 | 0.65 | -0.5 | 1.75 | 2020 | -0.16667 | 0 | 2020 | -0.8 | 1.8 | 2020 | -0.31034 | 0.11638
Fixed O&M (MUSD2020/MW/year) | FOM | 0.54 | 0.54 | 0.54 | 0.45 | 0.54 | 0.4 | 0.54 |  | -0.16667 | 0 | -0.19668 | 0 | -0.25926 | 0 | 2050 | -0.25926 | 0 | 2050 | -0.8125 | 0.5625 | 2050 | -0.38667 | 1.3467
Variable O&M (USD2020/MWh) | VOM | 2 | 1.8 | 1.6 | 0.4 | 5.6 | 0.3 | 2.5 |  | -0.8 | 1.8 | -0.80484 | 1.3875 | -0.8125 | 0.5625 | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%)
Energy Storage Expansion Cost (MUSD2020/MWh) | ESE | 0.232 | 0.142 | 0.075 | 0.16 | 0.259 | 0.046 | 0.176 |  | -0.31034 | 0.11638 | -0.33566 | 0.52733 | -0.38667 | 1.3467 | 2020 | -0.11111 | 0.88889 | 2020 | -0.15152 | 0.75758 | 2020 | -0.28571 | 0.14286
Output Capacity Expansion Cost (MUSD2020/MW) | OCE | 0.27 | 0.16 | 0.06 | 0.24 | 0.51 | 0.04 | 0.25 |  | -0.11111 | 0.88889 | -0.18436 | 1.6483 | -0.33333 | 3.1667 | 2050 | -0.33333 | 3.1667 | 2050 | -0.375 | 2.875 | 2050 | -0.6 | 0.4
Alternative Investment Cost (MUSD2020/MW) | AIC | 0.33 | 0.2 | 0.08 | 0.28 | 0.58 | 0.05 | 0.31 |  | -0.15152 | 0.75758 | -0.22501 | 1.4638 | -0.375 | 2.875 | Year | Lower (%) | Upper (%) | Year | Lower (%) | Upper (%)
Lifetime in Total Number of Cycles | LTN | 14000 | 30000 | 50000 | 10000 | 16000 | 20000 | 70000 |  | -0.28571 | 0.14286 | -0.39009 | 0.2277 | -0.6 | 0.4 | 2020 | -0.07619 | 0.33333 | 2020 | -0.069231 | 0.53846
Specific Energy (Wh/kg) | SE | 105 | 139 | 209 | 97 | 140 | 150 | 300 |  | -0.07619 | 0.33333 | -0.14448 | 0.36645 | -0.2823 | 0.43541 | 2050 | -0.2823 | 0.43541 | 2050 | -0.33462 | 0.53846
Energy Density (kWh/m3) | ED | 130 | 173 | 260 | 121 | 200 | 173 | 400 |  | -0.069231 | 0.53846 | -0.15738 | 0.53846 | -0.33462 | 0.53846
NOTE
Response time from idle to full-rated discharge (sec) | 1. The uncertainty is not available for this parameters, therefore it was repeated the data of 2020 and 2030
Response time from full-rated charge to full-rated discharge (sec)
Specific power (W/kg) | 1. This technical data was calculated with a Specific Power equation (see Lithium ion sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Power.
Power density (kW/m3) | 1. This technical data was calculated with a Power Density equation (see Lithium Ion sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Power Density.
1 | Samsung. ESS Batteries by Samsung SDI Top Safety & Reliability Solutions, (2018). http://www.samsungsdi.com/upload/ess_brochure/201809_SamsungSDI ESS_EN.pdf
2 | L. Kokam Co. Total Energy Storage Solution Provider, (2018). http://kokam.com/data/2018_Kokam_ESS_Brochure_ver_5.0.pdf
3 | L. Kokam Co. Kokam Li-ion / Polymer Cell, (2017). http://kokam.com/data/Kokam_Cell_Brochure_V.4.pdf
4 | StoraXe. StoraXe Industrial & Infrastructure Scalable battery storage system, (2018). https://www.ads-tec.de/fileadmin/download/doc/brochure/Datasheet_Energy_Industrial_EN.pdf
5 | Altairnano. 24 V 60 Ah Battery Module, (2016). https://altairnano.com/products/battery-module/
6 | Samsung, Smart Battery Systems for Energy Storage, (2016). http://www.samsungsdi.com/upload/ess_brochure/Samsung SDI brochure_EN.pdf
7 | Electropaedia. Battery Performance Characteristics - How to specify and test a battery, (2018). https://www.mpoweruk.com/performance.htm
8 | A.H. Fathima, K. Palanisamy. Renewable systems and energy storages for hybrid systems, Ed(s): A. Hina Fathima, et al., in Hybrid-renewable energy systems in microgrids. Woodhead Publishing (2018), pp. 162. https://doi.org/10.1016/B978-0-08-102493-5.00008-X
9 | Lazard. Levelized Cost of Storage (2017)., https://www.lazard.com/perspective/levelized-cost-of-storage-2017/
10 | LG Chem. Change your energy. Change your life., (2018). http://www.lgchem.com/upload/file/product/LGChem_Catalog_Global_2018.pdf
11 | Tesla. Addressing Peak Energy Demand with the Tesla Powerpack, (2016). https://www.tesla.com/da_DK/blog/addressing-peak-energy-demand-tesla-powerpack?redirect=no
12 | Tesla. Tesla Powerpack to Enable Large Scale Sustainable Energy to South Australia, (2017). https://www.tesla.com/da_DK/blog/Tesla-powerpack-enable-large-scale-sustainable-energy-south-australia?redirect=no Page
13 | Energy Storage Association. Frequency Regulation Services and a Firm Wind Product: AES Energy Storage Laurel Mountain Battery Energy Storage, (2018). http://energystorage.org/energy-storage/case-studies/frequency-regulation-services-and-firm-wind-product-aes-energy-storage
14 | Bloomberg New Energy Finance. New Energy Outlook 2018, (2018). https://bnef.turtl.co/story/neo2018.pdf?autoprint=true&teaser=true
15 | International Renewable Energy Agency. IRENA Battery Storage Report, (2015). http://www.irena.org/-/media/Files/IRENA/Agency/Publication/2015/IRENA_Battery_Storage_report_2015.pdf
16 | International Renewable Energy Agency. Electricity Storage and Renewables : Costs and Markets To 2030, (2017). http://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
17 | Danish Technological Institute. BESS project Smart grid ready Battery Energy Storage System for future grid, (2017). https://www.energiforskning.dk/sites/energiteknologi.dk/files/slutrapporter/bess_final_report_forskel_10731.pdf
18 | H. Chen, T.N. Cong, W. Yang, C. Tan, Y. Li, Y. Ding, Progress in electrical energy storage system: A critical review, Prog. Nat. Sci. 19 (2009) 291–312. doi:10.1016/j.pnsc.2008.07.014
19 | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127. doi:10.1016/j.apenergy.2017.06.046
20 | R. Benato, G. Bruno, F. Palone, R.M. Polito, M. Rebolini, Large-scale electrochemical energy storage in high voltage grids: Overview of the Italian experience, Energies. 10 (2017) 1-17. doi:10.3390/en10010108
21 | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596. doi:10.1016/j.rser.2014.10.011
22 | G. Huff, A.B. Currier, B.C. Kaun, D.M. Rastler, S.B. Chen, D.T. Bradshaw, W.D. Gauntlett, DOE/EPRI electricity storage handbook in collaboration with NRECA, (2015). https://www.sandia.gov/ess-ssl/publications/SAND2015-1002.pdf
23 | Danish Energy Agency. (2019). Technogy Data for Energy Storage. Copenhagen, Denmark. Retrieved from https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_energy_storage.pdf