## LA
Technology | Lead Acid battery
| 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2030) |  | Note | Ref
Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
Form of energy stored | Electro-chemical
Application | Frequency Restoration Reserve (2h)
Energy storage capacity for one unit (MWh) | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | [1]
Output capacity for one unit (MW) | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | [1]
Input capacity for one unit (MW) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | A
Round trip efficiency - DC (%) | 82 | 85 | 85 | 76 | 93 | 78 | 96 | B | [2], [3], [7]
- Charge efficiency (%) | 90.5539 | 92.1954 | 92.1954 | 87.178 | 96.4365 | 88.3176 | 97.9796
- Discharge efficiency (%) | 90.5539 | 92.1954 | 92.1954 | 87.178 | 96.4365 | 88.3176 | 97.9796
Energy losses during storage (%/day) | 0.3 | 0.3 | 0.3 | 0.1 | 0.4 | 0.1 | 0.4 |  | [6]
Forced outage (%) | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | C
Planned outage (weeks per year) | 0.2 | 0.1 | 0.1 | 0.1 | 0.3 | 0 | 0.2 | D
Technical lifetime (years) | 13 | 13 | 13 | 4.3333 | 21.798 | 4.3333 | 21.798 | average | [3],[4], [6], [7]
Construction time (years) | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | [3]
Lifetime in total number of cycles | 1900 | 3200 | 9600 | 300 | 3100 | 1000 | 5000 |  | [1]
Regulation ability
Response time from idle to full-rated discharge (sec) | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | E
Response time from full-rated charge to full-rated discharge (sec) | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |  | [4]
Financial data
Specific investment (MUSD$2020 per MWh) | 0.5535 | 0.33224 | 0.11984 | 0.38489 | 0.76441 | 0.23009 | 0.46069
- energy component (MUSD/MWh) | 0.216 | 0.1318 | 0.049223 | 0.0862 | 0.3881 | 0.0527 | 0.2372 | F | [1]
- capacity component (MUSD$/MW) | 0.675 | 0.40088 | 0.14123 | 0.59737 | 0.75263 | 0.35478 | 0.44698 | G | [3], [1]
- other project costs (MUSD$/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed O&M (kUSD2020/MW/year) | 3.774 | 3.774 | 3.774 | 3.552 | 14.43 | 3.552 | 14.43 |  | [5]
Variable O&M ($USD2020/MWh/year) | 0.4107 | 0.4107 | 0.4107 | 0.1665 | 0.5772 | 0.1665 | 0.5772 |  | [5]
Technology specific data
Alternative Investment cost (M$USD2020/MW) | 1.107 | 0.66448 | 0.23967 | 0.76977 | 1.5288 | 0.46018 | 0.92138
Specific power (W/kg) | 22.2321 | 29.6429 | 52.7049 | 14.6264 | 29.2528 | 23.7143 | 35.5714 | H | [8], [9]
Power density (kW/m3) | 55.6069 | 108.4334 | 214.0864 | 33.3641 | 77.8496 | 77.8496 | 139.0172 | H | [8], [9]
Specific energy (Wh/kg) | 44.4643 | 59.2857 | 105.4098 | 29.2528 | 58.5056 | 47.4286 | 71.1429 | H | [8], [9]
Energy density (kWh/m3) | 111.2137 | 216.8668 | 428.1729 | 66.7282 | 155.6992 | 155.6992 | 278.0343 | H | [8], [9]
Notes:
A | Assumed to be the same as output
B | IRENA has a slightly increasing projection, but only starts at 82%. Several studies mention a range between 84% to 86%, an average of 85% is commonly assumed for today.
C | It is assumed that no forced outage is necessary due to the maturity level of the technology
D | Flooded lead-acid batteries require refilling, for which the outage however could be reduced over time due to automation. The bigger valve-regulated lead-acid batteries do not require refilling. Values are assumed based on comparison with Li-Ion battery sheet
E | Assumed to be in the range of full-rated response time
F | This data is interpreted within the IRENA tool as: "Energy Installation cost". But also estimated by: Total Storage Invest/Installed Storage Capacity
G | The central data is based on values from [3], while uncertainty ranges correspond to the relative span of values from [1]
H | Array 1660 Ah, 48 VDC, 79,68 kWh (8x4)
References
[1] | IRENA (2017). Electricity storage and renewables: Costs and markets to 2030. Cost of service tool. Available in: https://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[2] | Luo, X., Wang, J., Dooner, M., & Clarke, J. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation. Applied Energy, 137, 511–536. https://doi.org/https://doi.org/10.1016/j.apenergy.2014.09.081
[3] | Schmidt, O., Melchior, S., Hawkes, A., & Staffell, I. (2019). Projecting the Future Levelized Cost of Electricity Storage Technologies. Joule, 3(1), 81–100. https://doi.org/10.1016/j.joule.2018.12.008
[4] | May, G. J., Davidson, A., & Monahov, B. (2018). Lead batteries for utility energy storage: A review. Journal of Energy Storage, 15, 145–157. https://doi.org/10.1016/j.est.2017.11.008
[5] | Zakeri, B., & Syri, S. (2015). Electrical energy storage systems: A comparative life cycle cost analysis. Renewable and Sustainable Energy Reviews, 42, 569–596. https://doi.org/10.1016/j.rser.2014.10.011
[6] | https://www.irena.org/-/media/Files/IRENA/Agency/Events/2017/Mar/15/2017_Kairies_Battery_Cost_and_Performance_01.pdf
[7] | Lazard levelized cost of storage 2016
[8] | Fullriver Battery. https://www.wholesalesolar.com/cms/fullriver-dc400-6-agm-battery-specs-4017212128.pdf
[9] | EASE/EERA. (2013). European Energy Storage Technology Development Roadmap Toward 2030. Retrieved from https://www.eera-set.eu/wp-content/uploads/148885-EASE-recommendations-Roadmap-04.pdf

## Data
[8 empty] | Exchange ratio between the years 2020 and 2030 |  | Exchange ratio between the years 2030 and 2050 | Reference | Prodecure followed to determine the projection | Projection in according with the exchange ratio (2020-2030 and 2030-2050)
Technical Data | ABB | 2015 | 2016 | 2017 | 2020 | 2025 | 2030 | 20 - 30 | 2050 | 30 - 50 |  |  | 2020 | 2030 | 2050 | C-rate
Energy Storage Capacity for One Unit (MWh) | ESC |  |  |  | 30 |  | 30 |  | 30 |  | [1] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [9] for batteries. 2. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Output Capacity for One Unit (MW) | OCO |  |  |  | 15 |  | 15 |  | 15 | [6 empty] | 0.5
Input Capacity for One Unit (MW) | ICO |  |  |  | 15 |  | 15 |  | 15
Round Trip Efficiency (%) | RTE |  |  |  | 82 |  | 85 |  | 85 |  |  | 1. The data of years 2015, 2020, 2030, and 2050 was obtained from [3]
Charge Efficiency (%) | CE |  |  |  | 90.5539 |  | 92.1954 |  | 92.1954 |  |  | 1. This technical data was calculated with equation round trip efficiency (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Round Trip Efficiency.
Discharge Efficiency (%) | DE |  |  |  | 90.5539 |  | 92.1954 |  | 92.1954
Energy Losses during Storage (%/day) | ELS |  | 0.3 |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | [6] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [9] for batteries. 2. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Forced Outage (%) | FO |  |  |  | 0 |  | 0 |  | 0 |  |  | 1. There no available data. 2. It is assumed that no forced outage is necessary due to the maturity level of the technology
Planned Outage (weeks per year) | PO |  |  |  | 0.2 |  | 0.1 |  | 0.1 |  |  | 1. There no available data. 2. Flooded lead-acid batteries require refilling, for which the outage however could be reduced over time due to automation. The bigger valve-regulated lead-acid batteries do not require refilling. Values are assumed based on comparison with Li-Ion battery sheet
Technical Lifetime (years) | TL | 10 | 14.5 | 15 | 13 |  | 17.3044 |  | 23.733 |  | [1], [3], [4], [7] | 1. The data for 2020 in the sheet called "LA" is the average of several authors (as shown [1], [3], [4], [7]). 2. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Construction Time (years) | CT | 1 |  |  | 1 |  | 1 |  | 1 |  | [3] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [3] for batteries. 2. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Response Time from Idle to Full-Rated Discharge (sec) | RTI |  |  |  | 0.001 |  | 0.001 |  | 0.001
Response Time from Full-Rated Charge to Full-Rated Discharge (sec) | RTF |  |  |  | 0.001 |  | 0.001 |  | 0.001
Specific Investment (MUSD2015 per MWh) | SI |  | 0.5775 |  | 0.4738 | 0.369 | 0.2888 |  | 0.10715 |  |  | 1. This parameter data was calculated with an equation for Specific Investment (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Investment.
Energy Component (MUSD2015 per MWh) | EC |  | 0.2625 |  | 0.2156 | 0.1686 | 0.1318 |  | 0.049223 |  | [1] | 1. The trend of the data for these parameters (in this case exponential decrease) was identified in reference [1] for batteries. 2. The data of years 2016, 2020, 2025, and 2030 was obtained from [1]. 3. The projection was estimated trough an exponential projection. See bottom flap called 17_EC.
Capacity Component (MUSD per MW) | CC |  | 0.105 |  | 0.0852 | 0.0656 | 0.0506 | -0.4061 | 0.017826 | -0.64771 |  | 1. The data of years 2016, 2020, 2025, and 2030 showed in this sheets from [1]. 2. The [1] values not including grid conenction are consequently very low. 3. The selected data for 2020 is a point data types from [3]. 4. The projections have a similar numerical behaviour to [1] with the value from [3] | 0.675 | 0.40088 | 0.14123
Fixed O&M (MUSD2020/MW/year) | FOM |  |  |  | 3.774 |  | 3.774 |  | 3.774 |  | [5] | 1. The data for these parameters was identified in reference [5] for batteries, see Table A4. This value is in European currency. The currency conversion to USD currency is in a factor of 1.11. 2. There no available data to estimate trend. Consequently, the data for the year 2020 is repeated for 2030 and 2050.
Variable O&M (MUSD2020/MW/year) | VOM |  |  |  | 0.4107 |  | 0.4107 |  | 0.4107
Alternative Investment Cost (MUSD2020 per MW) | AIC |  |  |  | 1.107 |  | 0.66448 |  | 0.23967 |  |  | 1. This data was calculated with an Alternative Investment Cost equation (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Alternative Investment Cost.
Lifetime in Total Number of Cycle | LTN |  | 1500 |  | 1866 | 2453 | 3225 |  | 9625.6334 |  | [1] | 1. The trend of the data for these parameters (in this case exponential increase) was identified in reference [1] for batteries. 2. The data of years 2016, 2020, 2025, and 2030 was obtained from [1] 3. The projection was estimated trough an exponential projection. See bottom flap called 22_LTN.
Specific Power (W/kg) | SP |  |  |  | 18.75 |  | 25 |  | 44.4499 |  | [8], [9] | 1. This technical data was calculated with a Specific Power equation (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Power. | 22.2321 | 29.6429 | 52.7049
Power Density (kW/m3) | PD |  |  |  | 50 |  | 97.5 |  | 192.5 |  |  | 1. This technical data was calculated with a Power Density equation (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Power Density. | 55.6069 | 108.4334 | 214.0864
Specific Energy (Wh/kg) | SE |  |  |  | 37.5 |  | 50 | 0.33333 | 88.8998 | 0.778 |  | 1. The data of years 2020 and 2030 was obtained from [9]. 2. The projection was estimated trough an exponential projection. See bottom flap called 25_SE. 3. The selected data for 2020 is a point data types from [8]. 4. The projections have a similar numerical behaviour to [9] with the value from [8] | 44.4643 | 59.2857 | 105.4098
Energy Density (kWh/m3) | ED |  |  |  | 100 |  | 195 | 0.95 | 385 | 0.97436 |  | 1. The data of years 2020 and 2030 was obtained from [9]. 2. The projection was estimated trough an linear projection. See bottom flap called 26_ED. 3. The selected data for 2020 is a point data types from [8]. 4. The projections have a similar numerical behaviour to [9] with the value from [8] | 111.2137 | 216.8668 | 428.1729
Cálculo de peso, volumen y energía para Specific Energy and Energy Density
Dimensions for array 1660 Ah, 48 VDC, 79,68 kWh (8x4) battery
|  | Weight | 1792 | kg |  | H | 0.424 | m
|  | Volume | 0.71646 | m3 |  | W | 0.716 | m
|  | Energy | 79.68 | kWh |  | L | 2.36 | m
References
[1] | IRENA (2017). Electricity storage and renewables: Costs and markets to 2030. Cost of service tool. Available in: https://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[2] | Luo, X., Wang, J., Dooner, M., & Clarke, J. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation. Applied Energy, 137, 511–536. https://doi.org/https://doi.org/10.1016/j.apenergy.2014.09.081
[3] | Schmidt, O., Melchior, S., Hawkes, A., & Staffell, I. (2019). Projecting the Future Levelized Cost of Electricity Storage Technologies. Joule, 3(1), 81–100. https://doi.org/10.1016/j.joule.2018.12.008
[4] | May, G. J., Davidson, A., & Monahov, B. (2018). Lead batteries for utility energy storage: A review. Journal of Energy Storage, 15, 145–157. https://doi.org/10.1016/j.est.2017.11.008
[5] | Zakeri, B., & Syri, S. (2015). Electrical energy storage systems: A comparative life cycle cost analysis. Renewable and Sustainable Energy Reviews, 42, 569–596. https://doi.org/10.1016/j.rser.2014.10.011
[6] | https://www.irena.org/-/media/Files/IRENA/Agency/Events/2017/Mar/15/2017_Kairies_Battery_Cost_and_Performance_01.pdf
[7] | Lazard levelized cost of storage 2016
[8] | Fullriver Battery. https://www.wholesalesolar.com/cms/fullriver-dc400-6-agm-battery-specs-4017212128.pdf
[9] | EASE/EERA. (2013). European Energy Storage Technology Development Roadmap Toward 2030. Retrieved from https://www.eera-set.eu/wp-content/uploads/148885-EASE-recommendations-Roadmap-04.pdf
Note on B44: Christoph Wolter: Please rewrite the reference as in the other chapters

## Uncertanties
|  |  | 2020 (Uncertainty) |  | 2030 (Uncertainty) |  |  | Exchange ratio 2020 |  | Exchange ratio 2030 |  | NOTE
Technical Data | 2020 | 2030 | Lower | Upper | Lower | Upper | Reference | Lower | Upper | Lower | Upper | 1. The uncertainty is calculated with the similar numerical behaviour from [1]
Technical Lifetime (years) | 9.9 | 12.8 | 3.3 | 16.6 | 4.3 | 21.3 | [1] | -0.66667 | 0.67677 | -0.25743 | 0.35248
Specific Energy (Wh/kg) | 38 | 50 | 25 | 50 | 40 | 60 | [9] | -0.34211 | 0.31579 | -0.2 | 0.2 | 1. The uncertainty is calculated with the similar numerical behaviour from [9]
Energy Density (kWh/m3) | 100 | 195 | 60 | 140 | 140 | 250 |  | -0.4 | 0.4 | -0.28205 | 0.28205
NOTE
Energy storage capacity for one unit (MWh) | 1. The uncertainty for these parameters has the same behaviour to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is interpreted within the IRENA tool as "Usable Storage Capacity" and "Installed Storage Power". 3. The uncertainty is zero percentage because the lead acid is a technology maturity.
Output capacity for one unit (MW)
Input capacity for one unit (MW)
Round trip efficiency (%) | 1. The uncertainty for this parameter has the same behaviour to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is interpreted within the IRENA tool as "Round-trip efficiency".
- Charge efficiency (%) | 1. This technical data was calculated with equation round trip efficiency (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Round Trip Efficiency.
- Discharge efficiency (%)
Energy losses during storage (%/day) | 1. The uncertainty for this parameter has the same behaviour to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is interpreted within the IRENA tool as "Self-discharge".
Forced outage (%) | 1. The uncertainty for these parameters has the same behaviour to [9] because the design is based on the same operational capacities of the energy storage system.
Planned outage (weeks per year)
Construction time (years) | 1. The uncertainty is the same as [3], see Table S4 on Supplemental Information in this reference
Response time from idle to full-rated discharge (sec) | 1. The uncertainty is not available for this parameters, therefore it was repeated the data of 2020 and 2030. 2. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Response time from full-rated charge to full-rated discharge (sec)
Specific investment (MUSD2020 per MWh) | 1. This parameter data was calculated with an equation for Specific Investment (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Investment.
-Energy component (MUSD2020/MWh) | 1. The uncertainty for these parameters has the same behaviour to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is interpreted within the IRENA tool as "Energy Installation Cost"
-Capacity component (MUSD2020/MW) | 1. The uncertainty is the same as [3], see Table S4 on Supplemental Information in this reference
Fixed O&M (MUSD2020/MW/year) | 1. The uncertainty is the same as [5], to keep the consistency between data (see Table A4 in this reference)
Variable O&M (USD2020/MWh/year)
Alternative investment cost (MUSD2020 per MW) | 1. This data was calculated with an Alternative Investment Cost equation (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Alternative Investment Cost.
Lifetime in total number of cycles | 1. The uncertainty for these parameters has the same behaviour to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is interpreted within the IRENA tool as "Cycle life".
Specific power (W/kg) | 1. This technical data was calculated with a Specific Power equation (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Power.
Power density (kW/m3) | 1. This technical data was calculated with a Power Density equation (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Power Density.
[1] | IRENA (2017). Electricity storage and renewables: Costs and markets to 2030. Cost of service tool. Available in: https://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[2] | Luo, X., Wang, J., Dooner, M., & Clarke, J. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation. Applied Energy, 137, 511–536. https://doi.org/https://doi.org/10.1016/j.apenergy.2014.09.081
[3] | Schmidt, O., Melchior, S., Hawkes, A., & Staffell, I. (2019). Projecting the Future Levelized Cost of Electricity Storage Technologies. Joule, 3(1), 81–100. https://doi.org/10.1016/j.joule.2018.12.008
[4] | May, G. J., Davidson, A., & Monahov, B. (2018). Lead batteries for utility energy storage: A review. Journal of Energy Storage, 15, 145–157. https://doi.org/10.1016/j.est.2017.11.008
[5] | Zakeri, B., & Syri, S. (2015). Electrical energy storage systems: A comparative life cycle cost analysis. Renewable and Sustainable Energy Reviews, 42, 569–596. https://doi.org/10.1016/j.rser.2014.10.011
[6] | https://www.irena.org/-/media/Files/IRENA/Agency/Events/2017/Mar/15/2017_Kairies_Battery_Cost_and_Performance_01.pdf
[7] | Lazard levelized cost of storage 2016
[8] | Fullriver Battery. https://www.wholesalesolar.com/cms/fullriver-dc400-6-agm-battery-specs-4017212128.pdf
[9] | EASE/EERA. (2013). European Energy Storage Technology Development Roadmap Toward 2030. Retrieved from https://www.eera-set.eu/wp-content/uploads/148885-EASE-recommendations-Roadmap-04.pdf
Note on B36: Christoph Wolter: Please rewrite the reference as in the other chapters