## VRF
Technology | Vanadium Redox Battery (VRB)
| 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2030) |  | Note | Ref
Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
Form of energy stored
Application | Frequency Containment Reserve (4h)
Energy storage capacity for one unit (MWh) | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 | 6.65 |  | [1], Table 3
Output capacity for one unit (MW)* | 1.6625 | 1.6625 | 1.6625 | 1.6625 | 1.6625 | 1.6625 | 1.6625 |  | [1]
Input capacity for one unit (MW)* | 1.6625 | 1.6625 | 1.6625 | 1.6625 | 1.6625 | 1.6625 | 1.6625 |  | [1]
Round trip efficiency (%) | 73 | 73 | 73 | 58.0256 | 82.359 | 59.6222 | 84.4756 | average | [2], [3], [4], [5], [6]
- Charge efficiency (%) | 85.44 | 85.44 | 85.44 | 76.1746 | 90.7518 | 77.2154 | 91.9106
- Discharge efficiency (%) | 85.44 | 85.44 | 85.44 | 76.1746 | 90.7518 | 77.2154 | 91.9106 |  | [3]
Energy losses during storage (%/day) | 0.2 | 0.2 | 0.2 | 0 | 1 | 0 | 1 |  | [1]
Forced outage (%) | 0.5 | 0.5 | 0.5 | 0 | 5 | 0 | 5 | A | [2]
Planned outage (weeks per year) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | [2], [4]
Technical lifetime (years) | 14 | 14 | 14 | 4.2 | 16.1 | 4.6572 | 18.2 | average | [2], [3], [4]
Construction time (years) | 1 | 1 | 1 | 0.2 | 2 | 0.2 | 2 | B | [2]
Lifetime in total number of cycles | 13000 | 13000 | 13000 | 12000 | 14000 | 12000 | 14000 |  | [1]
Regulation ability
Response time from idle to full-rated discharge (sec) | 0.1 | 0.1 | 0.1 | 0.005 | 2 | 0.005 | 2 | C | [2]
Response time from full-rated charge to full-rated discharge (sec) | 0.07 | 0.07 | 0.07 | 0.004 | 1.4 | 0.004 | 1.4 | C | [2]
Financial data
Specific investment (MUSD2020 per MWh) | 0.60245 | 0.31875 | 0.11139 | 0.5079 | 1.2384 | 0.26554 | 0.62444
energy component (MUSD2020 per MWh) | 0.52115 | 0.2761 | 0.076931 | 0.445 | 1.092 | 0.234 | 0.549 | D | [1]
capacity component (MUSD2020 per MW) | 0.0852 | 0.0506 | 0.017826 | 0.0596 | 0.1534 | 0.0354 | 0.091 | E | [1]
- other project costs (MUSD/MWh) | 0.06 | 0.03 | 0.03 | 0.048 | 0.108 | 0.022694 | 0.052694 | F | [2]
Fixed O&M (kUSD/MW/year) | 9.435 | 4.1278 | 3.8919 | 3.774 | 19.203 | 1.6511 | 8.4013 | G | [8], [2]
Variable O&M (USD2020/kWh/year) | 0.999 | 0.999 | 0.999 | 0.222 | 2.3088 | 0.222 | 2.3088 |  | [8], [2]
Technology specific data
Alternative Investment cost (M$USD2020/MW) | 2.4098 | 1.275 | 0.44555 | 2.0316 | 4.9534 | 1.0622 | 2.4978
Specific power (W/kg) | 2.95 | 2.95 | 2.95 | 1.475 | 3.6875 | 1.475 | 3.6875
Power density (W/m3) | 2260 | 2260 | 2260 | 1130 | 2825 | 1130 | 2825 | average
Specific energy (Wh/kg) | 11.8 | 11.8 | 11.8 | 5.9 | 14.75 | 5.9 | 14.75 |  | [2]
Energy density (Wh/m3) | 9040 | 9040 | 9040 | 4520 | 11300 | 4520 | 11300 |  | [2]
Notes:
A | Some companies guarantee at least 99.5% uptime
B | Depends highly on the installation.
C | Time is less than 100 ms for idle situation with electrolyte in reaction stack and pumps on. Less the 1 s if electrolyte must first be pumped. Less than 1 min if pumps are not on. PCS might be limiting the response time.[2]
D | This data is interpreted within the IRENA tool as: "Energy Installation cost+(Power Installation Cost/4 hr)".
E | This data is interpreted within the IRENA tool as: "Power Installation cost".
F | Value for utility T&D installations with discharge time of 4 hours used.
G | 2020 value is taken from [8], while the projections follow the relative decrease in costs from [2], based on the 2020 value.
References
[1] | IRENA (2017). Electricity storage and renewables: Costs and markets to 2030. Cost of service tool. Available in: https://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[2] | Danish Energy Agency. (2019). Technogy Data for Energy Storage. Copenhagen, Denmark. Retrieved from https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_energy_storage.pdf
[3] | Luo, X., Wang, J., Dooner, M., & Clarke, J. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation. Applied Energy, 137, 511–536. https://doi.org/https://doi.org/10.1016/j.apenergy.2014.09.081
[4] | International Renewable Energy Agency. Electricity Storage and Renewables : Costs and Markets To 2030, (2017). http://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[5] | Lai, C. S., Jia, Y., Lai, L. L., Xu, Z., McCulloch, M. D., & Wong, K. P. (2017). A comprehensive review on large-scale photovoltaic system with applications of electrical energy storage. Renewable and Sustainable Energy Reviews, 78, 439–451
[6] | Schmidt, O., Melchior, S., Hawkes, A., & Staffell, I. (2019). Projecting the Future Levelized Cost of Electricity Storage Technologies. Joule, 3(1), 81–100. https://doi.org/10.1016/j.joule.2018.12.008
[7] | EASE/EERA. (2013). European Energy Storage Technology Development Roadmap Toward 2030. Retrieved from https://www.eera-set.eu/wp-content/uploads/148885-EASE-recommendations-Roadmap-04.pdf
[8] | Zakeri, B., & Syri, S. (2015). Electrical energy storage systems: A comparative life cycle cost analysis. Renewable and Sustainable Energy Reviews, 42, 569–596. https://doi.org/10.1016/j.rser.2014.10.011

## Data
[6 empty] | Exchange ratio between the years 2030 and 2020 |  | Exchange ratio between the years 2050 and 2030 |  | Prodecure followed to determine the projection | Projection in according with the exchange ratio (2030-2020 and 2050-2030) |  |  | Projection in according with the exchange ratio (2020-2030 and 2030-2050)
Technical Data | ABB | 2016 | 2020 | 2025 | 2030 | 30 - 20 | 2050 |  | Reference |  | 2020 | 2030 | 2050
Energy Storage Capacity for One Unit (MWh) | ESC | 6.65 | 6.65 | 6.65 | 6.65 |  | 6.65 |  | [1] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [2] for VRB batteries. 2. The data of years 2016, 2020, 2025, and 2030 was obtained from [1] and it is located within the IRENA tool as "Usable Storage Capacity" and "Installed Storage".
Output Capacity for One Unit (MW) | OCO | 1.66 | 1.66 | 1.66 | 1.66 |  | 1.66
Input Capacity for One Unit (MW) | ICO | 1.66 | 1.66 | 1.66 | 1.66 |  | 1.66
Round Trip Efficiency (%) | RTE |  | 73 |  | 73 |  | 73 |  | [2-6] | 1. The data for year 2020 is the average of several authors [2-6]. 2. It is considered these parameters will not have a variation in the period 2030-2050 due it technological maturity.
Charge Efficiency (%) | CE |  | 85.44 |  | 85.44 |  | 85.44 |  |  | 1. This technical data was calculated with an equation for Round Trip Efficiency. 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Round Trip Efficiency.
Discharge Efficiency (%) | DE |  | 85.44 |  | 85.44 |  | 85.44
Energy Losses during Storage (%/day) | ELS |  | 0.2 |  | 0.2 |  | 0.2 |  | [1] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [2] for VRB batteries. 2. The data of years 2016, 2020, 2025, and 2030 was obtained from [1] and it is located within the IRENA tool as "Self-discharge"
Forced Outage (%) | FO |  | 0.5 |  | 0.5 |  | 0.5 |  | [2] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [2] for VRB batteries. 2. The data of years 2020, 2030, and 2050 was obtained from [2].
Planned Outage (weeks per year) | PO |  | 0 |  | 0 |  | 0 |  | [2, 4] | 1. The data for year 2020 is the average of several authors [2, 4]. 2. It is considered these parameters will not have a variation in the period 2030-2050 due it technological maturity.
Technical Lifetime (years) | TL |  | 14 |  | 14 |  | 14 |  | [2], [3], [4] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [2] VRB for batteries. 2. The data for 2020 is the average of several authors (as shown [2-4])
Construction Time (years) | CT |  | 1 |  | 1 |  | 1 |  | [2] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [2] for batteries. 2. The data of years 2020, 2030, and 2050 was obtained from [2].
Response Time from Idle to Full-Rated Discharge (sec) | RTI |  | 0.1 |  | 0.1 |  | 0.1
Response Time from Full-Rated Charge to Full-Rated Discharge (sec) | RTF |  | 0.07 |  | 0.07 |  | 0.07
Specific Investment (MUSD2015 per MWh) | SI |  | 0.60242 |  | 0.31873 |  | 0.11138 |  | [1] | 1. This parameter data was calculated with an equation for Specific Investment. 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Investment.
Energy Component (MUSD2015 per MWh) | EC | 0.67463 | 0.52115 | 0.37875 | 0.2761 |  | 0.076931 |  |  | 1.The data of years 2016, 2020, 2025, and 2030 was obtained from [1]. 2. These data is located within the IRENA tool as "Energy installation cost" and "Power installation cost". 3. The exponential projection is determinated in bottom flap called 17_EC and 18_CC
Capacity Component (MUSD per MW) | CC | 0.105 | 0.0852 | 0.0656 | 0.0506 |  | 0.017826
Other Project Costs (MUSD/MWh) | OPC |  | 0.06 |  | 0.03 | -0.5 | 0.03 | 0 | [2] | 1. The trend of the data for these parameters (in this case exponential decrease) was identified in reference [2] for VRB batteries. 2. The data of years 2020, 2030, and 2050 were obtained from [2].
Fixed O&M (kUSD2020/MW/year) | FOM |  | 53.28 |  | 23.31 | -0.5625 | 21.978 | -0.057143 | [2] | 1. The data of years 2020, 2030, and 2050 showed in this sheets from [2]. 2. The selected data for 2020 is a point data types from [8] (see Table A9). 3. The projections have similar numerical behavior to [2] with the estimated exchange ratio applied to estimated the projection of the value from [8]. | 9.435 | 4.1278 | 3.8919 | 1. The data for 2020 is a point data types for this year, historical data is not available. 2. The projections have a similar numerical behaviour to the datasheet from DEA Catalogue
Variable O&M (MUSD2020/MW/year) | VOM |  | 0.999 |  | 0.999 | 0 | 0.999 | 0 |  |  | 0.999 | 0.999 | 0.999
Alternative Investment Cost (MUSD2015 per MW) | AIC |  | 2.4133 |  | 1.2768 |  | 0.44619 |  |  | 1. This data was calculated with an Alternative Investment Cost equation (see NaS sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Alternative Investment Cost.
Lifetime in total number of cycles | LTN | 13000 | 13000 | 13000 | 13000 |  | 13000 |  | [1] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [2] for VRB batteries. 2. The data of years 2016, 2020, 2025, and 2030 was obtained from [1] and it is localated within the IRENA tool as "Cyce life"
Specific power (W/kg) | SP |  | 2.9456 |  | 2.9456 |  | 2.9456 |  | [2] | 1. This technical data was calculated with a Specific Power equation (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Power.
Power density (W/L) | PD |  | 2256.6015 |  | 2256.6015 |  | 2256.6015 |  |  | 1. This technical data was calculated with a Specific Power equation (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Power.
Specific energy (Wh/kg) | SE |  | 11.8 |  | 11.8 |  | 11.8 |  |  | 2. The data of years 2020, 2030, and 2050 were obtained from [2].
Energy density (Wh/L) | ED |  | 9040 |  | 9040 |  | 9040
[1] | IRENA (2017). Electricity storage and renewables: Costs and markets to 2030. Cost of service tool. Available in: https://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[2] | Danish Energy Agency. (2019). Technogy Data for Energy Storage. Copenhagen, Denmark. Retrieved from https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_energy_storage.pdf
[3] | Luo, X., Wang, J., Dooner, M., & Clarke, J. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation. Applied Energy, 137, 511–536. https://doi.org/https://doi.org/10.1016/j.apenergy.2014.09.081
[4] | International Renewable Energy Agency. Electricity Storage and Renewables : Costs and Markets To 2030, (2017). http://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[5] | Lai, C. S., Jia, Y., Lai, L. L., Xu, Z., McCulloch, M. D., & Wong, K. P. (2017). A comprehensive review on large-scale photovoltaic system with applications of electrical energy storage. Renewable and Sustainable Energy Reviews, 78, 439–451
[6] | Schmidt, O., Melchior, S., Hawkes, A., & Staffell, I. (2019). Projecting the Future Levelized Cost of Electricity Storage Technologies. Joule, 3(1), 81–100. https://doi.org/10.1016/j.joule.2018.12.008
[7] | EASE/EERA. (2013). European Energy Storage Technology Development Roadmap Toward 2030. Retrieved from https://www.eera-set.eu/wp-content/uploads/148885-EASE-recommendations-Roadmap-04.pdf
[8] | Zakeri, B., & Syri, S. (2015). Electrical energy storage systems: A comparative life cycle cost analysis. Renewable and Sustainable Energy Reviews, 42, 569–596. https://doi.org/10.1016/j.rser.2014.10.011

## Uncertanties
|  |  |  | 2020 (Uncertainty) |  | 2050 (Uncertainty) |  |  | Exchange ratio 2020 |  | Exchange ratio 2030 |  | Exchange ratio 2050 |  | Year | Lower (%) | Upper (%) | [6 empty] | NOTE
Technical Data | 2020 | 2030 | 2050 | Lower | Upper | Lower | Upper | Reference | Lower | Upper | Lower | Upper | Lower | Upper | 2020 | -0.20513 | 0.12821 | Year | Lower (%) | Upper (%) |  |  |  | 1. The uncertainty is calculated with the similar numerical behaviour from [1]. 2. The exchange ratio for 2030 is estimated by linear regression between the exchange ratio 2020 and 2050.
Round Trip Efficiency (%) | 78 | 78 | 78 | 62 | 88 | 67 | 95 | [2] | -0.20513 | 0.12821 | -0.18326 | 0.1572 | -0.14103 | 0.21795 | 2050 | -0.14103 | 0.21795 | 2020 | -0.7 | 0.15 | Year | Lower (%) | Upper (%)
Technical Lifetime (years) | 20 | 20 | 20 | 6 | 23 | 8 | 32 |  | -0.7 | 0.15 | -0.66734 | 0.3 | -0.6 | 0.6 |  |  |  | 2050 | -0.6 | 0.6 | 2020 | -0.2 | 0.8
Other Project Cost (MUSD/MWh) | 0.05 | 0.03 | 0.03 | 0.04 | 0.09 | 0.02 | 0.05 |  | -0.2 | 0.8 | -0.24354 | 0.75646 | -0.33333 | 0.66667 | [6 empty] | 2050 | -0.33333 | 0.66667
Fixed O&M (MUSD2020/MW/year) | 9.435 | 4.1278 | 3.8919 | 3.774 | 19.203 |  |  |  | -0.6 | 1.0353 | -0.6 | 1.0353
NOTE
Energy storage capacity for one unit (MWh) | 1. The uncertainty for these parameters has the same to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is located within the IRENA tool as "Usable Storage Capacity" and "Installed storage power"
Output capacity for one unit (MW)
Input capacity for one unit (MW)
- Charge efficiency (%) | 1. This technical data was calculated with an equation for Round Trip Efficiency. 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Round Trip Efficiency.
- Discharge efficiency (%)
Energy losses during storage (%/day) | 1. The uncertainty for these parameters has the same to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is located within the IRENA tool as "Self-discharge"
Forced outage (%) | 1. The uncertainty for these parameters has the same to [2] because the design is based on the same operational capacities of the energy storage system.
Planned outage (weeks per year)
Construction time (years)
Response time from idle to full-rated discharge (sec)
Response time from full-rated charge to full-rated discharge (sec)
Specific investment (MUSD2020 per MWh) | 1. This parameter data was calculated with an equation for Specific Investment. 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Investment.
-Energy component (MUSD2020/MWh) | 1. The uncertainty for these parameters has the same to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is located within the IRENA tool as "Energy installation cost" and "Power installation cost"
-Capacity component (MUSD2020/MW)
Variable O&M (USD2020/MWh/year) | 1. The uncertainty for these parameters has the same to [8] because the design is based on the same operational capacities of the energy storage system
Alternative investment cost (MUSD2020 per MW) | 1. This data was calculated with an Alternative Investment Cost equation (see NaS sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Alternative Investment Cost.
Lifetime in total number of cycles | 1. The uncertainty for these parameters has the same to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is located within the IRENA tool as "Cycle life"
Specific power (W/kg) | 1. This technical data was calculated with a Specific Power equation (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Power.
Power density (kW/m3) | 1. This technical data was calculated with a Specific Power equation (see LA sheet). 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Power.
Specific energy (Wh/kg) | 1. The uncertainty for these parameters has the same to [2] because the design is based on the same operational capacities of the energy storage system.
Energy density (kWh/m3)