## CAES
Compressed Air Energy Storage
| 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2030) |  | Note | Ref
Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
Form of energy stored | Mechanical and chemical
Application | Energy Shifting
Energy storage capacity for one unit (MWh) | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 |  | [1]
Output capacity for one unit (MW) | 1060 | 1060 | 1060 | 1060 | 1060 | 1060 | 1060 |  | [1]
Input capacity for one unit (MW) | 1060 | 1060 | 1060 | 1060 | 1060 | 1060 | 1060 |  | [1]
Round trip efficiency (%) | 64 | 70.56 | 72.25 | 55.2 | 64 | 64 | 70.56 |  | [3]
- Charge efficiency (%) | 80 | 84 | 85 | 80 | 80 | 80 | 84 |  | [3]
- Discharge efficiency (%) | 80 | 84 | 85 | 69 | 80 | 80 | 84 |  | [3]
Energy losses during storage (%/day) | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0 | 0.5 |  | [2], [3], [9]
Auxiliary electricity consumption (% of output)
Forced outage (%) | 5 | 4 | 4 | 5 | 5 | 5 | 4 |  | [3]
Planned outage (weeks per year) | 5 | 4 | 3 | 5 | 5 | 5 | 4 |  | [3]
Technical lifetime (years) | 40 | 40 | 40 | 35 | 45 | 35 | 45 | Average | [3], [8], [9]
Construction time (years) | 3 | 3 | 3 | 2 | 3 | 2 | 3 |  | [3]
Lifetime (total number of cycles) | 50000 | 50000 | 50000 | 10000 | 100000 | 10000 | 100000 |  | [1]
Regulation ability
Idle to full discharge (sec) | 700 | 1000 | 1000 | 500 | 1000 | 740 | 1350 | F, G | [3]
Full charge to full discharge (sec)
Financial data
Specific investment (MUSD2020 per MWh) | 0.2384 | 0.22367 | 0.20592 | 0.13628 | 0.27837 | 0.13166 | 0.26015 |  | [1]
-Energy component (MUSD2020/MWh) | 0.048 | 0.0442 | 0.034357 | 0.002 | 0.077 | 0.002 | 0.071 | B | [1]
-Capacity component (MUSD2020/MW) | 0.781 | 0.6934 | 0.63002 | 0.331 | 0.869 | 0.294 | 0.771 | C | [1]
-Other project costs (MUSD/MWh) | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 | 0.093 |  | [9]
Fixed O&M (kUSD2020/MW/year) | 2.73 | 2.73 | 2.73 | 2.22 | 4.44 | 2.22 | 4.44 |  | [3]
Variable O&M (USD2020/MWh/year) | 2.73 | 2.73 | 2.73 | 2.22 | 3.3 | 2.2 | 3.3 | E | [3]
Technology specific data
Specific investment ((MUSD2020/MW) | 1.9117 | 1.7936 | 1.6513 | 1.0928 | 2.2322 | 1.0558 | 2.0861 |  | [1]
Notes
A | This data is interpreted within the IRENA tool as: "Total Invest per usable kWh storage", and is verifiable as a result of : Energy Storage + Power Conversion/Usable Storage Capacity.
B | This data is interpreted within the IRENA tool as: "Energy Installation cost".
C | This data is interpreted within the IRENA tool as: "Power Installation cost".
D | This data is interpreted within the IRENA tool as a result of : Maintenance/Installed conversion Power
E | Variable O&M cost can vary depending on the gas price in case of a CAES plant supported by a gas turbine.
F | If a CAES plant is operated as a hot spinning reserve, it can reach the maximum capacity within a few minutes. The emergency startup times from cold conditions at the Huntorf and McIntosh plants are about 5 minutes. Their normal startup times are about 10 to 12 minutes [3]
G | The obtainable ramping rate is likely to decrease after application of thermal energy storage. This is because the heat must be delivered to the storage material, which is a process that cannot be controlled independently.
References
[1] | IRENA (2017). Electricity storage and renewables: Costs and markets to 2030. Cost of service tool. Available in: https://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[2] | Huang, Y., Keatley, P., Chen, H. S., Zhang, X. J., Rolfe, A., & Hewitt, N. J. (2018). Techno-economic study of compressed air energy storage systems for the grid integration of wind power. International Journal of Energy Research, 42(2), 559–569. https://doi.org/10.1002/er.3840
[3] | Danish Energy Agency. (2019). Technogy Data for Energy Storage. Copenhagen, Denmark. Retrieved from https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_energy_storage.pdf
[4] | Kaldemeyer, C., Boysen, C., & Tuschy, I. (2016). Compressed Air Energy Storage in the German Energy System – Status Quo & Perspectives. Energy Procedia, 99, 298–313. https://doi.org/https://doi.org/10.1016/j.egypro.2016.10.120
[5] | Komarnicky, P., Lombardi, P., Styczynski, Z. (2017). Electric Energy Storage systems. Springer-Verlag GmbH Germany
[6] | Schmidt et al., Projecting the Future Levelized Cost of Electricity Storage TechnologiesJoule 3, 81–100. January 16, 2019 ª 2018 Elsevier Inc.
[7] | Gustavsson, J. (2016). Energy Storage Technology Comparison. KTH Industrial Engineering and Management. Retrieved from http://www.diva-portal.org/smash/get/diva2:953046/FULLTEXT01.pdf
[8] | Diaz-Gonzalez, F., Sumper, A., & Gomis-Bellmunt, O. (2016). Energy Storage Technologies. In Energy Storage in Power Systems (pp. 93–141). John Wiley & Sons, Ltd. https://doi.org/10.1002/9781118971291.ch4
[9] | IRENA, Battery storage technology improvements and cost reductions to 2030: A Deep Dive, March 2017, https://www.irena.org/-/media/Files/IRENA/Agency/Events/2017/Mar/15/2017_Kairies_Battery_Cost_and_Performance_01.pd
[10] | EASE/EERA. (2013). European Energy Storage Technology Development Roadmap Toward 2030. Retrieved from https://www.eera-set.eu/wp-content/uploads/148885-EASE-recommendations-Roadmap-04.pdf
[11] | Zakeri, B., & Syri, S. (2015). Electrical energy storage systems: A comparative life cycle cost analysis. Renewable and Sustainable Energy Reviews, 42, 569–596. https://doi.org/10.1016/j.rser.2014.10.011

## Data
Technical Data | ABB | 2015 | 2016 | 2017 | 2020 | 2025 | 2030 | 2050 | Reference | Prodecure followed to determine the projection
Energy Storage Capacity for One Unit (MWh) | ESC |  | 8500 |  | 8500 | 8500 | 8500 | 8500 | [1] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [1] for CAES. 2. This data is interpreted within the IRENA tool as "Usable Storage Capacity" and "Installed Storage". 3. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Output Capacity for One Unit (MW) | OCO |  | 1060 |  | 1060 | 1060 | 1060 | 1060
Input Capacity for One Unit (MW) | ICO |  | 1060 |  | 1060 | 1060 | 1060 | 1060
Round Trip Efficiency (%) | RTE |  |  |  | 64 |  | 70.56 | 72.25 |  | 1. The trend of the data for these parameters (in this case exponential growth) was identified in reference [3] for CAES. 2. This technical data was calculated with an equation for Round Trip Efficiency. 3. In the chapter of Introduccion of the Catalogue, it is defined the equation of Round Trip Efficiency.
Charge Efficiency (%) | CE | 80 |  |  | 80 |  | 84 | 85 | [3] | 1. The trend of the data is similar the reference [3]. 2. The data of years 2015, 2020, 2030, and 2050 was obtained from [3]
Discharge Efficiency (%) | DE | 69 |  |  | 80 |  | 84 | 85
Energy Losses during Storage (%/day) | ELS |  | 0.5 |  |  | 0.5 |  |  | [1] [3] | 1. The trend of the data for these parameters (in this case constant) was identified in reference [3] for CAES. 2. It is considered these parameters will not have a variation in the period 2020-2050 due it technological maturity.
Forced Outage (%) | FO | 5 |  |  | 5 |  | 4 | 4 | [3] | 1. The trend of the data is similar the reference [3]. 2. The data of years 2015, 2020, 2030, and 2050 was obtained from [3].
Planned Outage (weeks per year) | PO | 5 |  |  | 5 |  | 4 | 3
Technical Lifetime (years) | TL | 40 | 50 |  | 45 |  | 45 | 40 |  | 1. The trend of the data is similar the reference [3]. 2. The data of years 2015, 2020, 2030, and 2050 was obtained from [3].
Construction Time (years) | CT | 2.9 |  |  | 2.9 |  | 2.9 | 2.9
Response Time from Idle to Full-Rated Discharge (sec) | RTI | 700 |  |  | 700 |  | 1000 | 1000 |  | 1. The trend of the data is similar the reference [3]. 2. The data of years 2015, 2020, 2030, and 2050 was obtained from [3].
Specific Investment (MUSD2015 per MWh) | SI |  | 0.26335 |  | 0.23857 |  | 0.22367 | 0.20592 | [1] | 1. This data was calculated with a Specific Investment equation (see CAES sheet). 2.
Energy Component (MUSD2015 per MWh) | EC |  | 0.0525 |  | 0.0481 | 0.0457 | 0.0442 | 0.034357 |  | 1. The trend of the data for these parameters (in this case exponential decrease) was identified in reference [1] for CAES. 2. This data is interpreted within the IRENA tool as "Energy installation cost" 3. The data of years 2016, 2020, 2025, and 2030 was obtained from [1]. 4. See the exponential projection called 15_EC
Capacity Component (MUSD per MW) | CC |  | 0.945 |  | 0.7816 | 0.7127 | 0.6934 | 0.63002 |  | 1. The trend of the data for these parameters (in this case exponential decrease) was identified in reference [1] for CAES. 2. This data is interpreted within the IRENA tool as "Power installation cost" 3. The data of years 2016, 2020, 2025, and 2030 was obtained from [1]. 4. See the exponential projection called 16_CC. 5. The hyperbolic projection was for 2050 by learning curve
Other Project Costs (MUSD/MWh) | OPC | 0.093 | 0.093 |  | 0.093 |  | 0.093 | 0.093 | [9] | 1. The data obtained for year 2020 was obtained from [9], the trend is similar the reference [3] (in this case constant). 2. It is considered this parameter will not have a variation in the period 2020-2050 due it technological maturity.
Fixed O&M (MUSD2020/MW/year) | FOM |  | 2.73 |  | 2.73 |  | 2.73 | 2.73 | [3] | 1. The data obtained for year 2020 was obtained from [3], the trend is similar the reference [3] (in this case constant). 2. It is considered this parameter will not have a variation in the period 2020-2050 due it technological maturity.
Variable O&M (MUSD2020/MWh/year) | VOM |  | 2.73 |  | 2.73 |  | 2.73 | 2.73
Specific Investment (MUSD2020 per MW) | SI |  | 2.1117 |  | 1.9131 |  | 1.7936 | 1.6513 |  | 1. This technical data was calculated with an equation, see CAES sheet. 2. This technical data was calculated with an equation for Specific Investment. 3. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Investment.
|  | Hiperbolic regression of Capacity component |  |  | A que parametro corresponde esta tabla?? |  |  |  |  | No se ha nombrado las ecuaciones de las hojas 20_FOM, 21_VOM, 22_SI, URTI_L, URTI_U, donde las utiliza?? Si el primer paso fue revisar como se comportan los datos en un documento, tiene que verificaarse que los datos que se estan incluyendo correspondan con eso que se dice.
|  | x | y | y=1/(A+Bx)
| n | Año | Capacity Component (MUSD2015 per MW) | Y'=1/Y | XY' | X2 | B | A | y
| 1 | 2016 | 0.945 | 1.0582 | 2133.3333 | 4064256 | 0.02665 | -52.6099 | 0.89618
| 2 | 2020 | 0.7816 | 1.2794 | 2584.4422 | 4080400 |  |  | 0.81804
| 3 | 2025 | 0.7127 | 1.4031 | 2841.3077 | 4100625 |  |  | 0.73763
| 4 | 2030 | 0.6934 | 1.4422 | 2927.6031 | 4120900 |  |  | 0.67162
| Suma | 8091 |  | 5.1829 | 10486.6863 | 16366181 |  |  | 0.49458
| Prom | 2022.75 |  | 1.2957
| DEA | Delta years | Approximation of Capacity Component (MUSD/MW) | Est. Learning curve | 92.4%
| start | 1 | 0.945 | Explanation: The learning curve approach is not dependent simply on the years passing, but on technology development. Here it is assumed, that the growth in potential capacity is linear over time, i.e. compared to the amount of years passing. This is only a simplification, as technology generally matures dependent on their actual construction and implementation. But since the components that CAES consists of are prone to individual technology development, you can still use this approach as simplified regression. Generally, a learning rate factor of 10% is applied for non-emerging technologies. Here, a factor lower than this, i.e. 7.6%, leads to a good acceptable fit, which can be explained by the strong maturity of the capacity components (compressor & generator etc.) used by CAES.
|  | 5 | 0.78655
|  | 10 | 0.72677
|  | 15 | 0.69393
| 2050 | 35 | 0.63002
[1] | IRENA (2017). Electricity storage and renewables: Costs and markets to 2030. Cost of service tool. Available in: https://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[2] | Huang, Y., Keatley, P., Chen, H. S., Zhang, X. J., Rolfe, A., & Hewitt, N. J. (2018). Techno-economic study of compressed air energy storage systems for the grid integration of wind power. International Journal of Energy Research, 42(2), 559–569. https://doi.org/10.1002/er.3840
[3] | Danish Energy Agency. (2019). Technogy Data for Energy Storage. Copenhagen, Denmark. Retrieved from https://ens.dk/sites/ens.dk/files/Analyser/technology_data_catalogue_for_energy_storage.pdf
[4] | Kaldemeyer, C., Boysen, C., & Tuschy, I. (2016). Compressed Air Energy Storage in the German Energy System – Status Quo & Perspectives. Energy Procedia, 99, 298–313. https://doi.org/https://doi.org/10.1016/j.egypro.2016.10.120
[5] | Komarnicky, P., Lombardi, P., Styczynski, Z. (2017). Electric Energy Storage systems. Springer-Verlag GmbH Germany
[6] | Schmidt et al., Projecting the Future Levelized Cost of Electricity Storage TechnologiesJoule 3, 81–100. January 16, 2019 ª 2018 Elsevier Inc.
[7] | Gustavsson, J. (2016). Energy Storage Technology Comparison. KTH Industrial Engineering and Management. Retrieved from http://www.diva-portal.org/smash/get/diva2:953046/FULLTEXT01.pdf
[8] | Diaz-Gonzalez, F., Sumper, A., & Gomis-Bellmunt, O. (2016). Energy Storage Technologies. In Energy Storage in Power Systems (pp. 93–141). John Wiley & Sons, Ltd. https://doi.org/10.1002/9781118971291.ch4
[9] | IRENA, Battery storage technology improvements and cost reductions to 2030: A Deep Dive, March 2017, https://www.irena.org/-/media/Files/IRENA/Agency/Events/2017/Mar/15/2017_Kairies_Battery_Cost_and_Performance_01.pd
[10] | EASE/EERA. (2013). European Energy Storage Technology Development Roadmap Toward 2030. Retrieved from https://www.eera-set.eu/wp-content/uploads/148885-EASE-recommendations-Roadmap-04.pdf

## Uncertanties
[5 empty] | 2020 (Uncertainty) |  | 2050 (Uncertainty) |  |  | Exchange ratio 2020 |  | Exchange ratio 2030 |  | Exchange ratio 2050 |  | Year | Lower (%) | Upper (%) | Note
Technical Data | 2015 | 2020 | 2030 | 2050 | Lower | Upper | Lower | Upper | Reference | Lower | Upper | Lower | Upper | Lower | Upper | 2020 | -0.28571 | 0.42857 | 1. The uncertainty is calculated with the similar numerical behaviour from [3]. 2. The exchange ratio for 2030 is estimated by linear regression between the exchange ratio 2020 and 2050.
Response Time from Idle to Full-Rated Discharge (sec) | 700 | 700 | 1000 | 1000 | 500 | 1000 | 800 | 1200 | [3] | -0.28571 | 0.42857 | -0.25743 | 0.35248 | -0.2 | 0.2 | 2050 | -0.2 | 0.2
NOTE
Energy storage capacity for one unit (MWh) | 1. The uncertainty for these parameters has the same behaviour to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is interpreted within the IRENA tool as "Usable Storage Capacity" and "Installed Storage Power". 3. The uncertainty is zero percentage because the CAES is a technology maturity.
Output capacity for one unit (MW)
Input capacity for one unit (MW)
Round trip efficiency (%) | 1. The uncertainty was calculated with an equation for Round Trip Efficiency. 2. In the chapter of Introduccion of the Catalogue, it is defined the equation of Round Trip Efficiency.
- Charge efficiency (%) | 1. The uncertainty for these parameters has the same behaviour to [3] to keep the consistency between data.
- Discharge efficiency (%)
Energy losses during storage (%/day) | 1. The uncertainty for this parameter has the same behaviour to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is interpreted within the IRENA tool as "Self-discharge"
Forced outage (%) | 1. The uncertainty for these parameters has the same behaviour to [3] to keep the consistency between data.
Planned outage (weeks per year)
Technical lifetime (years)
Construction time (years)
Specific investment (MUSD2020 per MWh) | 1. The uncertainty for these parameters has the same behaviour to [1] because the design is based on the same operational capacities of the energy storage system. 2. This data is interpreted within the IRENA tool as "Energy installation cost" and "Power installation cost"
-Energy component (MUSD2020/MWh)
-Capacity component (MUSD2020/MW)
-Other project costs (MUSD/MWh) | 1. The uncertainty for this parameter has the same behaviour to [9] because the design is based on the same operational capacities of the energy storage system. 2. The uncertainty is zero percentage because the CAES is a technology maturity.
Fixed O&M (MUSD2020/MW/year) | 1. The uncertainty for these parameters has the same behaviour to [11] because the design is based on the same operational capacities of the energy storage system, see Table A2 of this reference
Variable O&M (USD2020/MWh/year)
Specific investment (MUSD2020 per MW) | 1. The uncertainty was calculated with an equation (see CAES sheet). 2. This technical data was calculated with an equation for Specific Investment. 3. In the chapter of Introduccion of the Catalogue, it is defined the equation of Specific Investment.